## Hourly Solar Gains
Hourly Solar Heat Gains for May-December for Chennai, IN (13°N; 16°N Considered)
Month |  |  | SC | CLF
W/m2
Jan | 1.296 | 94.63 | 0.55 | 0.51 | 34.4007
Feb | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Mar | 1.296 | 110.41 | 0.55 | 0.51 | 40.1371
Apr | 1.296 | 123.02 | 0.55 | 0.51 | 44.7212
May | 1.296 | 164.03 | 0.55 | 0.51 | 59.6295
Jun | 1.296 | 208.2 | 0.55 | 0.51 | 75.6865
July | 1.296 | 173.5 | 0.55 | 0.51 | 63.0721
Aug | 1.296 | 129.33 | 0.55 | 0.51 | 47.0151
Sep | 1.296 | 113.56 | 0.55 | 0.51 | 41.2822
Oct | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Nov | 1.296 | 94.63 | 0.55 | 0.51 | 34.4007
Dec | 1.296 | 91.48 | 0.55 | 0.51 | 33.2555
Hourly Solar Heat Gains for May-December for Ahmedabad, IN (23°N; 24°N Considered)
Month |  |  | SC | CLF
W/m2
Jan | 1.296 | 85.17 | 0.55 | 0.51 | 30.9617
Feb | 1.296 | 94.63 | 0.55 | 0.51 | 34.4007
Mar | 1.296 | 107.25 | 0.55 | 0.51 | 38.9884
Apr | 1.296 | 116.71 | 0.55 | 0.51 | 42.4274
May | 1.296 | 135.64 | 0.55 | 0.51 | 49.3089
Jun | 1.296 | 173.5 | 0.55 | 0.51 | 63.0721
July | 1.296 | 141.95 | 0.55 | 0.51 | 51.6028
Aug | 1.296 | 119.87 | 0.55 | 0.51 | 43.5761
Sep | 1.296 | 110.41 | 0.55 | 0.51 | 40.1371
Oct | 1.296 | 97.79 | 0.55 | 0.51 | 35.5494
Nov | 1.296 | 85.17 | 0.55 | 0.51 | 30.9617
Dec | 1.296 | 82.01 | 0.55 | 0.51 | 29.8129
Hourly Solar Heat Gains for May-December for Delhi, IN (28.7°N; 32°N Considered)
Month |  |  | SC | CLF
W/m2
Jan | 1.296 | 75.71 | 0.55 | 0.51 | 27.5227
Feb | 1.296 | 85.17 | 0.55 | 0.51 | 30.9617
Mar | 1.296 | 100.94 | 0.55 | 0.51 | 36.6945
Apr | 1.296 | 113.56 | 0.55 | 0.51 | 41.2822
May | 1.296 | 119.87 | 0.55 | 0.51 | 43.5761
Jun | 1.296 | 138.8 | 0.55 | 0.51 | 50.4577
July | 1.296 | 126.18 | 0.55 | 0.51 | 45.87
Aug | 1.296 | 116.71 | 0.55 | 0.51 | 42.4274
Sep | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Oct | 1.296 | 88.32 | 0.55 | 0.51 | 32.1068
Nov | 1.296 | 75.71 | 0.55 | 0.51 | 27.5227
Dec | 1.296 | 69.4 | 0.55 | 0.51 | 25.2288
Hourly Solar Heat Gains for May-December for Bangkok, TH (13.75°N, 16°N Considered)
Month |  |  | SC | CLF
W/m2
Jan | 1.296 | 94.63 | 0.55 | 0.51 | 34.4007
Feb | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Mar | 1.296 | 110.41 | 0.55 | 0.51 | 40.1371
Apr | 1.296 | 123.02 | 0.55 | 0.51 | 44.7212
May | 1.296 | 164.03 | 0.55 | 0.51 | 59.6295
Jun | 1.296 | 208.2 | 0.55 | 0.51 | 75.6865
July | 1.296 | 173.5 | 0.55 | 0.51 | 63.0721
Aug | 1.296 | 129.33 | 0.55 | 0.51 | 47.0151
Sep | 1.296 | 113.56 | 0.55 | 0.51 | 41.2822
Oct | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Nov | 1.296 | 94.63 | 0.55 | 0.51 | 34.4007
Dec | 1.296 | 91.48 | 0.55 | 0.51 | 33.2555
Hourly Solar Heat Gains for May-December for Colombo, SL (6.9°N; 8°N Considered)
Month |  |  | SC | CLF
W/m2
Jan | 1.296 | 100.94 | 0.55 | 0.51 | 36.6945
Feb | 1.296 | 107.25 | 0.55 | 0.51 | 38.9884
Mar | 1.296 | 116.71 | 0.55 | 0.51 | 42.4274
Apr | 1.296 | 138.8 | 0.55 | 0.51 | 50.4577
May | 1.296 | 233.43 | 0.55 | 0.51 | 84.8583
Jun | 1.296 | 283.91 | 0.55 | 0.51 | 103.2092
July | 1.296 | 242.9 | 0.55 | 0.51 | 88.301
Aug | 1.296 | 148.26 | 0.55 | 0.51 | 53.8967
Sep | 1.296 | 199.87 | 0.55 | 0.51 | 72.6583
Oct | 1.296 | 110.41 | 0.55 | 0.51 | 40.1371
Nov | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Dec | 1.296 | 97.79 | 0.55 | 0.51 | 35.5494
Hourly Solar Heat Gains for May-December for Dhaka, BD (23.8 °N; 24°N Considered)
Month |  |  | SC | CLF
W/m2
Jan | 1.296 | 85.17 | 0.55 | 0.51 | 30.9617
Feb | 1.296 | 94.63 | 0.55 | 0.51 | 34.4007
Mar | 1.296 | 107.25 | 0.55 | 0.51 | 38.9884
Apr | 1.296 | 116.71 | 0.55 | 0.51 | 42.4274
May | 1.296 | 135.64 | 0.55 | 0.51 | 49.3089
Jun | 1.296 | 173.5 | 0.55 | 0.51 | 63.0721
July | 1.296 | 141.95 | 0.55 | 0.51 | 51.6028
Aug | 1.296 | 119.87 | 0.55 | 0.51 | 43.5761
Sep | 1.296 | 110.41 | 0.55 | 0.51 | 40.1371
Oct | 1.296 | 97.79 | 0.55 | 0.51 | 35.5494
Nov | 1.296 | 85.17 | 0.55 | 0.51 | 30.9617
Dec | 1.296 | 82.01 | 0.55 | 0.51 | 29.8129
Hourly Solar Heat Gains for May-December for Ho Chi Min City, VE (10°N; 16°N Considered)
Month |  |  | SC | CLF
W/m2
Jan | 1.296 | 94.63 | 0.55 | 0.51 | 34.4007
Feb | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Mar | 1.296 | 110.41 | 0.55 | 0.51 | 40.1371
Apr | 1.296 | 123.02 | 0.55 | 0.51 | 44.7212
May | 1.296 | 164.03 | 0.55 | 0.51 | 59.6295
Jun | 1.296 | 208.2 | 0.55 | 0.51 | 75.6865
July | 1.296 | 173.5 | 0.55 | 0.51 | 63.0721
Aug | 1.296 | 129.33 | 0.55 | 0.51 | 47.0151
Sep | 1.296 | 113.56 | 0.55 | 0.51 | 41.2822
Oct | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Nov | 1.296 | 94.63 | 0.55 | 0.51 | 34.4007
Dec | 1.296 | 91.48 | 0.55 | 0.51 | 33.2555
Hourly Solar Heat Gains for May-December for Manila, PE (14.5°N, 16°N Considered)
Month |  |  | SC | CLF
W/m2
Jan | 1.296 | 94.63 | 0.55 | 0.51 | 34.4007
Feb | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Mar | 1.296 | 110.41 | 0.55 | 0.51 | 40.1371
Apr | 1.296 | 123.02 | 0.55 | 0.51 | 44.7212
May | 1.296 | 164.03 | 0.55 | 0.51 | 59.6295
Jun | 1.296 | 208.2 | 0.55 | 0.51 | 75.6865
July | 1.296 | 173.5 | 0.55 | 0.51 | 63.0721
Aug | 1.296 | 129.33 | 0.55 | 0.51 | 47.0151
Sep | 1.296 | 113.56 | 0.55 | 0.51 | 41.2822
Oct | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Nov | 1.296 | 94.63 | 0.55 | 0.51 | 34.4007
Dec | 1.296 | 91.48 | 0.55 | 0.51 | 33.2555
Hourly Solar Heat Gains for May-December for Jakarta, ID (6°S, 8°N Considered)
Month |  |  | SC | CLF
W/m2
Jan | 1.296 | 100.94 | 0.55 | 0.51 | 36.6945
Feb | 1.296 | 107.25 | 0.55 | 0.51 | 38.9884
Mar | 1.296 | 116.71 | 0.55 | 0.51 | 42.4274
Apr | 1.296 | 138.8 | 0.55 | 0.51 | 50.4577
May | 1.296 | 233.43 | 0.55 | 0.51 | 84.8583
Jun | 1.296 | 283.91 | 0.55 | 0.51 | 103.2092
July | 1.296 | 242.9 | 0.55 | 0.51 | 88.301
Aug | 1.296 | 148.26 | 0.55 | 0.51 | 53.8967
Sep | 1.296 | 119.87 | 0.55 | 0.51 | 43.5761
Oct | 1.296 | 110.41 | 0.55 | 0.51 | 40.1371
Nov | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Dec | 1.296 | 97.79 | 0.55 | 0.51 | 35.5494
Hourly Solar Heat Gains for May-December for Myanmar MM (16.8°N, 16°N Considered)
Month |  |  | SC | CLF
W/m2
Jan | 1.296 | 94.63 | 0.55 | 0.51 | 34.4007
Feb | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Mar | 1.296 | 110.41 | 0.55 | 0.51 | 40.1371
Apr | 1.296 | 123.02 | 0.55 | 0.51 | 44.7212
May | 1.296 | 164.03 | 0.55 | 0.51 | 59.6295
Jun | 1.296 | 208.2 | 0.55 | 0.51 | 75.6865
July | 1.296 | 173.5 | 0.55 | 0.51 | 63.0721
Aug | 1.296 | 129.33 | 0.55 | 0.51 | 47.0151
Sep | 1.296 | 113.56 | 0.55 | 0.51 | 41.2822
Oct | 1.296 | 104.1 | 0.55 | 0.51 | 37.8433
Nov | 1.296 | 94.63 | 0.55 | 0.51 | 34.4007
Dec | 1.296 | 91.48 | 0.55 | 0.51 | 33.2555

## India Dengue Season ugr& uso_
Balance Point Temperature, Annual Variable Degree Days, Thermal Load of Living Space and Annual Electricity Consumption Calculations for No Insulation (Indian Electrical Grid Mix and Solar Electricity) for Baseline Scenario (Low Dengue Risk AC Temperature Zone (22-25°C) for all Three Climate Scenarios in India
|  | Chennai (Warm and Humid Climate) | [32 empty] | LDRZ Use Temperature Setpoint Preference %
|  | Month | [7 empty] | Tbal-m calc | Tbal-m used | VCDDmth | AC hrs/24 hrs (fAC) | Conv (24/1000) KWh |  |  | Annual VCDD | TLBE-r-x |  |  | Annual VCDD | TLBE-f-x |  |  | Annual VCDD | TLBE-wallop-x | All Other Heat Loads | BE+Other Loads | 10%SF | TATL-x | EER | AC Setpt- Elec Cons (KWh) | Avg Elec Cons (KWh) |  | AC Setpoint Temp (°C) | % Preference | Adj. Pref %
|  | Jun | 18 | 75.6865 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.7104 | 15 | 525.5 | [22 empty] | 18 | 6 | 0.09375
|  | Jul | 18 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.7742 | 15 | 486.9 | [22 empty] | 19 | 1 | 0.015625
|  | Aug | 18 | 47.0151 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.8554 | 15 | 478 | [22 empty] | 20 | 7 | 0.10938
|  | Sep | 18 | 41.2822 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.8844 | 15 | 468.1 | [22 empty] | 21 | 4 | 0.0625
|  | Oct | 18 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.9018 | 15 | 446.7 | [22 empty] | 22 | 16 | 0.25
|  | Nov | 18 | 34.4007 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.9192 | 15 | 372.8 | [22 empty] | 23 | 10 | 0.15625
|  | VCDD-18 Deg | [9 empty] | 2778 | 0.375 | 0.024 | 3.59 | 12.96 | 2778 | 1163.2531 | 3.94 | 12.96 | 2778 | 1276.6621 | 2.13 | 41.904 | 2778 | 2231.5665 | 1275.5767 | 5947.0584 | 594.7058 | 6541.7642 | 3.1 | 2110 |  | 18 | 24 | 20 | 0.3125
|  | Jun | 19 | 75.6865 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.7104 | 16 | 495.5 | [23 empty] | 64
|  | Jul | 19 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.7742 | 16 | 455.9
|  | Aug | 19 | 47.0151 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.8554 | 16 | 447
|  | Sep | 19 | 41.2822 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.8844 | 16 | 438.1
|  | Oct | 19 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.9018 | 16 | 415.7
|  | Nov | 19 | 34.4007 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.9192 | 16 | 342.8
|  | VCDD-19 Deg | [9 empty] | 2595 | 0.375 | 0.024 | 3.59 | 12.96 | 2595 | 1086.6241 | 3.94 | 12.96 | 2595 | 1192.5624 | 2.13 | 41.904 | 2595 | 2084.5627 | 1253.7425 | 5617.4916 | 561.7492 | 6179.2408 | 3.1 | 1993 |  | 19
|  | Jun | 20 | 75.6865 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.7104 | 17 | 465.5
|  | Jul | 20 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.7742 | 17 | 424.9
|  | Aug | 20 | 47.0151 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.8554 | 17 | 416
|  | Sep | 20 | 41.2822 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.8844 | 17 | 408.1
|  | Oct | 20 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.9018 | 17 | 384.7
|  | Nov | 20 | 34.4007 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.9192 | 17 | 312.8
|  | VCDD-20 Deg | [9 empty] | 2412 | 0.375 | 0.024 | 3.59 | 12.96 | 2412 | 1009.9951 | 3.94 | 12.96 | 2412 | 1108.4626 | 2.13 | 41.904 | 2412 | 1937.5588 | 1231.9083 | 5287.9248 | 528.7925 | 5816.7173 | 3.1 | 1876 |  | 20
|  | Jun | 21 | 75.6865 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.7104 | 18 | 435.5
|  | Jul | 21 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.7742 | 18 | 393.9
|  | Aug | 21 | 47.0151 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.8554 | 18 | 385
|  | Sep | 21 | 41.2822 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.8844 | 18 | 378.1
|  | Oct | 21 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.9018 | 18 | 353.7
|  | Nov | 21 | 34.4007 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.9192 | 18 | 282.8
|  | VCDD-21 Deg | [9 empty] | 2229 | 0.375 | 0.024 | 3.59 | 12.96 | 2229 | 933.3661 | 3.94 | 12.96 | 2229 | 1024.3628 | 2.13 | 41.904 | 2229 | 1790.555 | 1210.0741 | 4958.358 | 495.8358 | 5454.1938 | 3.1 | 1759 |  | 21
|  | Jun | 22 | 75.6865 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.7104 | 19 | 405.5
|  | Jul | 22 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.7742 | 19 | 362.9
|  | Aug | 22 | 47.0151 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.8554 | 19 | 354
|  | Sep | 22 | 41.2822 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.8844 | 19 | 348.1
|  | Oct | 22 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.9018 | 19 | 322.7
|  | Nov | 22 | 34.4007 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.9192 | 19 | 252.8
|  | VCDD-22 Deg | [9 empty] | 2046 | 0.375 | 0.024 | 3.59 | 12.96 | 2046 | 856.7371 | 3.94 | 12.96 | 2046 | 940.263 | 2.13 | 41.904 | 2046 | 1643.5511 | 1188.2399 | 4628.7912 | 462.8791 | 5091.6703 | 3.1 | 1642 |  | 22
|  | Jun | 23 | 75.6865 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.7104 | 20 | 375.5
|  | Jul | 23 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.7742 | 20 | 331.9
|  | Aug | 23 | 47.0151 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.8554 | 20 | 323
|  | Sep | 23 | 41.2822 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.8844 | 20 | 318.1
|  | Oct | 23 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.9018 | 20 | 291.7
|  | Nov | 23 | 34.4007 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.9192 | 20 | 222.8
|  | VCDD-23 Deg | [9 empty] | 1863 | 0.375 | 0.024 | 3.59 | 12.96 | 1863 | 780.1081 | 3.94 | 12.96 | 1863 | 856.1633 | 2.13 | 41.904 | 1863 | 1496.5473 | 1166.5916 | 4299.4103 | 429.941 | 4729.3513 | 3.1 | 1526 |  | 23
|  | Jun | 24 | 75.6865 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.7104 | 21 | 345.5
|  | Jul | 24 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.7742 | 21 | 300.9
|  | Aug | 24 | 47.0151 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.8554 | 21 | 292
|  | Sep | 24 | 41.2822 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.8844 | 21 | 288.1
|  | Oct | 24 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.9018 | 21 | 260.7
|  | Nov | 24 | 34.4007 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.9192 | 21 | 192.8
|  | VCDD-24 Deg | [9 empty] | 1680 | 0.375 | 0.024 | 3.59 | 12.96 | 1680 | 703.4792 | 3.94 | 12.96 | 1680 | 772.0635 | 2.13 | 41.904 | 1680 | 1349.5435 | 1144.7136 | 3969.7997 | 396.98 | 4366.7797 | 3.1 | 1409 |  | 24
|  | Total Energy Consumption for Operation of AC Unit Between Setpoint Temperature of 18-24°C (Based on User Setpoint Preferences) for Chennai (Warm and Humid) | [30 empty] | 1633
Ahmedabad (Hot and Dry)
|  | Month | [7 empty] | Tbal-m calc | Tbal-m used | VCDDmth
|  | Jun | 18 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.7742 | 15 | 532.9
|  | Jul | 18 | 51.6028 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.8322 | 15 | 432.9
|  | Aug | 18 | 43.5761 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.8728 | 15 | 393.7
|  | Sep | 18 | 40.1371 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.8902 | 15 | 391.5
|  | Oct | 18 | 35.5494 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.9134 | 15 | 437.2
|  | Nov | 18 | 30.9617 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.9366 | 15 | 307
|  | VCDD-18 Deg | [9 empty] | 2495.2 | 0.375 | 0.024 | 3.59 | 12.96 | 2495.2 | 1044.8341 | 3.94 | 12.96 | 2495.2 | 1146.6981 | 2.13 | 41.904 | 2495.2 | 2004.3934 | 1294.8554 | 5490.781 | 549.0781 | 6039.8591 | 3.1 | 1948
|  | Jun | 19 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.7742 | 16 | 502.9
|  | Jul | 19 | 51.6028 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.8322 | 16 | 401.9
|  | Aug | 19 | 43.5761 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.8728 | 16 | 362.7
|  | Sep | 19 | 40.1371 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.8902 | 16 | 361.5
|  | Oct | 19 | 35.5494 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.9134 | 16 | 406.2
|  | Nov | 19 | 30.9617 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.9366 | 16 | 277
|  | VCDD-19 Deg | [9 empty] | 2312.2 | 0.375 | 0.024 | 3.59 | 12.96 | 2312.2 | 968.2051 | 3.94 | 12.96 | 2312.2 | 1062.5983 | 2.13 | 41.904 | 2312.2 | 1857.3895 | 1273.0212 | 5161.2142 | 516.1214 | 5677.3356 | 3.1 | 1831
|  | Jun | 20 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.7742 | 17 | 472.9
|  | Jul | 20 | 51.6028 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.8322 | 17 | 370.9
|  | Aug | 20 | 43.5761 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.8728 | 17 | 331.7
|  | Sep | 20 | 40.1371 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.8902 | 17 | 331.5
|  | Oct | 20 | 35.5494 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.9134 | 17 | 375.2
|  | Nov | 20 | 30.9617 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.9366 | 17 | 247.5
|  | VCDD-20 Deg | [9 empty] | 2129.7 | 0.375 | 0.024 | 3.59 | 12.96 | 2129.7 | 891.7855 | 3.94 | 12.96 | 2129.7 | 978.7283 | 2.13 | 41.904 | 2129.7 | 1710.7873 | 1251.187 | 4832.4882 | 483.2488 | 5315.737 | 3.1 | 1715
|  | Jun | 21 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.7742 | 18 | 442.9
|  | Jul | 21 | 51.6028 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.8322 | 18 | 339.9
|  | Aug | 21 | 43.5761 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.8728 | 18 | 300.7
|  | Sep | 21 | 40.1371 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.8902 | 18 | 301.5
|  | Oct | 21 | 35.5494 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.9134 | 18 | 344.2
|  | Nov | 21 | 30.9617 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.9366 | 18 | 218.7
|  | VCDD-21 Deg | [9 empty] | 1947.9 | 0.375 | 0.024 | 3.59 | 12.96 | 1947.9 | 815.659 | 3.94 | 12.96 | 1947.9 | 895.18 | 2.13 | 41.904 | 1947.9 | 1564.7474 | 1229.3528 | 4504.9393 | 450.4939 | 4955.4332 | 3.1 | 1599
|  | Jun | 22 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.7742 | 19 | 412.9
|  | Jul | 22 | 51.6028 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.8322 | 19 | 308.9
|  | Aug | 22 | 43.5761 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.8728 | 19 | 269.7
|  | Sep | 22 | 40.1371 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.8902 | 19 | 271.5
|  | Oct | 22 | 35.5494 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.9134 | 19 | 313.2
|  | Nov | 22 | 30.9617 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.9366 | 19 | 191.3
|  | VCDD-22 Deg | [9 empty] | 1767.5 | 0.375 | 0.024 | 3.59 | 12.96 | 1767.5 | 740.1187 | 3.94 | 12.96 | 1767.5 | 812.2751 | 2.13 | 41.904 | 1767.5 | 1419.8322 | 1207.5186 | 4179.7446 | 417.9745 | 4597.7191 | 3.1 | 1483
|  | Jun | 23 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.7742 | 20 | 382.9
|  | Jul | 23 | 51.6028 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.8322 | 20 | 277.9
|  | Aug | 23 | 43.5761 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.8728 | 20 | 238.7
|  | Sep | 23 | 40.1371 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.8902 | 20 | 241.5
|  | Oct | 23 | 35.5494 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.9134 | 20 | 282.2
|  | Nov | 23 | 30.9617 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.9366 | 20 | 165.2
|  | VCDD-23 Deg | [9 empty] | 1588.4 | 0.375 | 0.024 | 3.59 | 12.96 | 1588.4 | 665.1228 | 3.94 | 12.96 | 1588.4 | 729.9676 | 2.13 | 41.904 | 1588.4 | 1275.9612 | 1185.6844 | 3856.7361 | 385.6736 | 4242.4097 | 3.1 | 1369
|  | Jun | 24 | 63.0721 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.7742 | 21 | 352.9
|  | Jul | 24 | 51.6028 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.8322 | 21 | 246.9
|  | Aug | 24 | 43.5761 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.8728 | 21 | 207.7
|  | Sep | 24 | 40.1371 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.8902 | 21 | 211.5
|  | Oct | 24 | 35.5494 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.9134 | 21 | 251.2
|  | Nov | 24 | 30.9617 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.9366 | 21 | 141.5
|  | VCDD-24 Deg | [9 empty] | 1411.7 | 0.375 | 0.024 | 3.59 | 12.96 | 1411.7 | 591.1319 | 3.94 | 12.96 | 1411.7 | 648.7631 | 2.13 | 41.904 | 1411.7 | 1134.0182 | 1163.8502 | 3537.7633 | 353.7763 | 3891.5397 | 3.1 | 1255
|  | Total Energy Consumption for Operation of AC Unit Between Setpoint Temperature of 18-24°C (Based on User Setpoint Preferences) for Ahmedabad (Hot and Dry) | [30 empty] | 1476
Delhi (Composite)
|  | Month | [7 empty] | Tbal-m calc | Tbal-m used | VCDDmth
|  | Jun | 18 | 50.4577 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.838 | 15 | 607.5
|  | Jul | 18 | 45.87 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.8612 | 15 | 511.4
|  | Aug | 18 | 42.4274 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.8786 | 15 | 458.6
|  | Sep | 18 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.9018 | 15 | 420.9
|  | Oct | 18 | 32.1068 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.9308 | 15 | 382.9
|  | Nov | 18 | 27.5227 | 420 | 118.8 | 36 | 189.27 | 8.47 | 14.954 | 15 | 182.1
|  | VCDD-18 Deg | [9 empty] | 2563.4 | 0.375 | 0.024 | 3.59 | 12.96 | 2563.4 | 1073.392 | 3.94 | 12.96 | 2563.4 | 1178.0402 | 2.13 | 41.904 | 2563.4 | 2059.1784 | 1285.0299 | 5595.6405 | 559.564 | 6155.2045 | 3.1 | 1986
|  | Jun | 19 | 50.4577 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.838 | 16 | 577.5
|  | Jul | 19 | 45.87 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.8612 | 16 | 480.4
|  | Aug | 19 | 42.4274 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.8786 | 16 | 427.6
|  | Sep | 19 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.9018 | 16 | 390.9
|  | Oct | 19 | 32.1068 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.9308 | 16 | 351.9
|  | Nov | 19 | 27.5227 | 420 | 118.8 | 36 | 189.27 | 8.47 | 15.954 | 16 | 157.7
|  | VCDD-19 Deg | [9 empty] | 2386 | 0.375 | 0.024 | 3.59 | 12.96 | 2386 | 999.1079 | 3.94 | 12.96 | 2386 | 1096.514 | 2.13 | 41.904 | 2386 | 1916.673 | 1265.8638 | 5278.1588 | 527.8159 | 5805.9746 | 3.1 | 1873
|  | Jun | 20 | 50.4577 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.838 | 17 | 547.5
|  | Jul | 20 | 45.87 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.8612 | 17 | 449.4
|  | Aug | 20 | 42.4274 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.8786 | 17 | 396.6
|  | Sep | 20 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.9018 | 17 | 360.9
|  | Oct | 20 | 32.1068 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.9308 | 17 | 320.9
|  | Nov | 20 | 27.5227 | 420 | 118.8 | 36 | 189.27 | 8.47 | 16.954 | 17 | 134.3
|  | VCDD-20 Deg | [9 empty] | 2209.6 | 0.375 | 0.024 | 3.59 | 12.96 | 2209.6 | 925.2426 | 3.94 | 12.96 | 2209.6 | 1015.4473 | 2.13 | 41.904 | 2209.6 | 1774.971 | 1246.6978 | 4962.3587 | 496.2359 | 5458.5945 | 3.1 | 1761
|  | Jun | 21 | 50.4577 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.838 | 18 | 517.5
|  | Jul | 21 | 45.87 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.8612 | 18 | 418.4
|  | Aug | 21 | 42.4274 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.8786 | 18 | 365.6
|  | Sep | 21 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.9018 | 18 | 330.9
|  | Oct | 21 | 32.1068 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.9308 | 18 | 289.9
|  | Nov | 21 | 27.5227 | 420 | 118.8 | 36 | 189.27 | 8.47 | 17.954 | 18 | 112.9
|  | VCDD-21 Deg | [9 empty] | 2035.2 | 0.375 | 0.024 | 3.59 | 12.96 | 2035.2 | 852.2148 | 3.94 | 12.96 | 2035.2 | 935.2998 | 2.13 | 41.904 | 2035.2 | 1634.8755 | 1224.8636 | 4647.2536 | 464.7254 | 5111.979 | 3.1 | 1649
|  | Jun | 22 | 50.4577 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.838 | 19 | 487.5
|  | Jul | 22 | 45.87 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.8612 | 19 | 387.4
|  | Aug | 22 | 42.4274 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.8786 | 19 | 334.6
|  | Sep | 22 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.9018 | 19 | 300.9
|  | Oct | 22 | 32.1068 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.9308 | 19 | 258.9
|  | Nov | 22 | 27.5227 | 420 | 118.8 | 36 | 189.27 | 8.47 | 18.954 | 19 | 93.6
|  | VCDD-22 Deg | [9 empty] | 1862.9 | 0.375 | 0.024 | 3.59 | 12.96 | 1862.9 | 780.0663 | 3.94 | 12.96 | 1862.9 | 856.1173 | 2.13 | 41.904 | 1862.9 | 1496.467 | 1203.0294 | 4335.6799 | 433.568 | 4769.2479 | 3.1 | 1538
|  | Jun | 23 | 50.4577 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.838 | 20 | 457.5
|  | Jul | 23 | 45.87 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.8612 | 20 | 356.4
|  | Aug | 23 | 42.4274 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.8786 | 20 | 303.6
|  | Sep | 23 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.9018 | 20 | 270.9
|  | Oct | 23 | 32.1068 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.9308 | 20 | 228
|  | Nov | 23 | 27.5227 | 420 | 118.8 | 36 | 189.27 | 8.47 | 19.954 | 20 | 77.2
|  | VCDD-23 Deg | [9 empty] | 1693.6 | 0.375 | 0.024 | 3.59 | 12.96 | 1693.6 | 709.174 | 3.94 | 12.96 | 1693.6 | 778.3135 | 2.13 | 41.904 | 1693.6 | 1360.4683 | 1185.7295 | 4033.6854 | 403.3685 | 4437.0539 | 3.1 | 1431
|  | Jun | 24 | 50.4577 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.838 | 21 | 427.5
|  | Jul | 24 | 45.87 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.8612 | 21 | 325.4 | [15 empty] | T
|  | Aug | 24 | 42.4274 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.8786 | 21 | 272.6
|  | Sep | 24 | 37.8433 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.9018 | 21 | 240.9
|  | Oct | 24 | 32.1068 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.9308 | 21 | 197.7
|  | Nov | 24 | 27.5227 | 420 | 118.8 | 36 | 189.27 | 8.47 | 20.954 | 21 | 62.8
|  | VCDD-24 Deg | [9 empty] | 1526.9 | 0.375 | 0.024 | 3.59 | 12.96 | 1526.9 | 639.3704 | 3.94 | 12.96 | 1526.9 | 701.7046 | 2.13 | 41.904 | 1526.9 | 1226.5583 | 1168.4297 | 3736.063 | 373.6063 | 4109.6693 | 3.1 | 1326
|  | Total Energy Consumption for Operation of AC Unit Between Setpoint Temperature of 18-24°C (Based on User Setpoint Preferences) for Delhi (Composite) | [30 empty] | 1534
CLTDgw-avg (°C) for AC Opn hrs. |  | Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid)
06.00-07.00 | -1 | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
07.00-08.00 | -1 | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 18 | 7.5 | 4.6 | 15.1 | 3.75 | 1.296 | 270 | 19.8142
08.00-09.00 | 0 | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 18 | 7.5 | 3.55 | 14.05 | 3.75 | 1.296 | 279 | 19.051
17.00-18.00 | 7 | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 18 | 7.5 | 2.55 | 13.05 | 3.75 | 1.296 | 279 | 17.695
18.00-19.00 | 7 | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 18 | 7.5 | 1.75 | 12.25 | 3.75 | 1.296 | 270 | 16.0745
19.00-20.00 | 6 | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 18 | 7.5 | 1.25 | 11.75 | 3.75 | 1.296 | 279 | 15.9323
20.00-21.00 | 4 | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 18 | 7.5 | -1.25 | 9.25 | 3.75 | 1.296 | 270 | 12.1379
21.00-22.00 | 3 | TLgw-CHN (KWh)-18 Deg | [12 empty] | 100.7048
22.00-23.00 | 2 | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 19 | 6.5 | 4.6 | 14.1 | 3.75 | 1.296 | 270 | 18.502
CLTDgw-avg (°C) | 3 | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 19 | 6.5 | 3.55 | 13.05 | 3.75 | 1.296 | 279 | 17.695
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 19 | 6.5 | 2.55 | 12.05 | 3.75 | 1.296 | 279 | 16.3391
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 19 | 6.5 | 1.75 | 11.25 | 3.75 | 1.296 | 270 | 14.7623
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 19 | 6.5 | 1.25 | 10.75 | 3.75 | 1.296 | 279 | 14.5764
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 19 | 6.5 | -1.25 | 8.25 | 3.75 | 1.296 | 270 | 10.8256
|  | TLgw-CHN (KWh)-19 Deg | [12 empty] | 92.7004
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 20 | 5.5 | 4.6 | 13.1 | 3.75 | 1.296 | 270 | 17.1898
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 20 | 5.5 | 3.55 | 12.05 | 3.75 | 1.296 | 279 | 16.3391
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 20 | 5.5 | 2.55 | 11.05 | 3.75 | 1.296 | 279 | 14.9831
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 20 | 5.5 | 1.75 | 10.25 | 3.75 | 1.296 | 270 | 13.4501
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 20 | 5.5 | 1.25 | 9.75 | 3.75 | 1.296 | 279 | 13.2204
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 20 | 5.5 | -1.25 | 7.25 | 3.75 | 1.296 | 270 | 9.5135
|  | TLgw-CHN (KWh)-20 Deg | [12 empty] | 84.6959
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 21 | 4.5 | 4.6 | 12.1 | 3.75 | 1.296 | 270 | 15.8776
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 21 | 4.5 | 3.55 | 11.05 | 3.75 | 1.296 | 279 | 14.9831
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 21 | 4.5 | 2.55 | 10.05 | 3.75 | 1.296 | 279 | 13.6272
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 21 | 4.5 | 1.75 | 9.25 | 3.75 | 1.296 | 270 | 12.1379
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 21 | 4.5 | 1.25 | 8.75 | 3.75 | 1.296 | 279 | 11.8645
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 21 | 4.5 | -1.25 | 6.25 | 3.75 | 1.296 | 270 | 8.2012
|  | TLgw-CHN (KWh)-21 Deg | [12 empty] | 76.6915
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 22 | 3.5 | 4.6 | 11.1 | 3.75 | 1.296 | 270 | 14.5654
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 22 | 3.5 | 3.55 | 10.05 | 3.75 | 1.296 | 279 | 13.6272
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 22 | 3.5 | 2.55 | 9.05 | 3.75 | 1.296 | 279 | 12.2713
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 22 | 3.5 | 1.75 | 8.25 | 3.75 | 1.296 | 270 | 10.8256
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 22 | 3.5 | 1.25 | 7.75 | 3.75 | 1.296 | 279 | 10.5085
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 22 | 3.5 | -1.25 | 5.25 | 3.75 | 1.296 | 270 | 6.8891
|  | TLgw-CHN (KWh)-22 Deg | [12 empty] | 68.6871
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 23 | 2.5 | 4.6 | 10.1 | 3.75 | 1.296 | 270 | 13.2532
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 23 | 2.5 | 3.55 | 9.05 | 3.75 | 1.296 | 279 | 12.2713
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 23 | 2.5 | 2.55 | 8.05 | 3.75 | 1.296 | 279 | 10.9153
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 23 | 2.5 | 1.75 | 7.25 | 3.75 | 1.296 | 270 | 9.5135
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 23 | 2.5 | 1.25 | 6.75 | 3.75 | 1.296 | 279 | 9.1526
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 23 | 2.5 | -1.25 | 4.25 | 3.75 | 1.296 | 279 | 5.7627
|  | TLgw-CHN (KWh)-23 Deg | [12 empty] | 60.8686
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 24 | 1.5 | 4.6 | 9.1 | 3.75 | 1.296 | 270 | 11.941
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 24 | 1.5 | 3.55 | 8.05 | 3.75 | 1.296 | 279 | 10.9153
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 24 | 1.5 | 2.55 | 7.05 | 3.75 | 1.296 | 279 | 9.5594
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 24 | 1.5 | 1.75 | 6.25 | 3.75 | 1.296 | 270 | 8.2012
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 24 | 1.5 | 1.25 | 5.75 | 3.75 | 1.296 | 279 | 7.7967
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 24 | 1.5 | -1.25 | 3.25 | 3.75 | 1.296 | 279 | 4.4068
|  | TLgw-CHN (KWh)-24 Deg | [12 empty] | 52.8204
Annual Radiation Thermal Load Through Glass Window- Chennai
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jun | 0.55 | 0.51 | 208.2 | 1.296 | 270 | 20.4354
|  | Jul | 0.55 | 0.51 | 173.5 | 1.296 | 279 | 17.5971
|  | Aug | 0.55 | 0.51 | 129.33 | 1.296 | 279 | 13.1172
|  | Sep | 0.55 | 0.51 | 113.56 | 1.296 | 270 | 11.1462
|  | Oct | 0.55 | 0.51 | 104.1 | 1.296 | 279 | 10.5583
|  | Nov | 0.55 | 0.51 | 94.63 | 1.296 | 270 | 9.2882
|  | Tlrad-CHN | [5 empty] | 82.1423
Inflitration Load for Different Setpoint Temperatures for Chennai
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 18 | 20.4 | 618.404 | 0.277 | 171.2979 | 270 | 46.2504
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 18 | 19 | 575.9645 | 0.277 | 159.5422 | 279 | 44.5123
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 18 | 17.9 | 542.6192 | 0.277 | 150.3055 | 279 | 41.9352
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 18 | 17 | 515.3366 | 0.277 | 142.7482 | 270 | 38.542
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 18 | 16 | 485.0227 | 0.277 | 134.3513 | 279 | 37.484
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 18 | 13.2 | 400.1437 | 0.277 | 110.8398 | 270 | 29.9268
|  | Tinf for setpoint 18 degrees C | [11 empty] | 238.6507
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 19 | 19.4 | 588.09 | 0.277 | 162.9009 | 270 | 43.9833
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 19 | 18 | 545.6506 | 0.277 | 151.1452 | 279 | 42.1695
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 19 | 16.9 | 512.3052 | 0.277 | 141.9086 | 279 | 39.5925
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 19 | 16 | 485.0227 | 0.277 | 134.3513 | 270 | 36.2748
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 19 | 15 | 454.7088 | 0.277 | 125.9543 | 279 | 35.1413
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 19 | 12.2 | 369.8298 | 0.277 | 102.4429 | 270 | 27.6596
|  | Tinf for setpoint 21 degrees C | [11 empty] | 224.8209
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 20 | 18.4 | 557.7761 | 0.277 | 154.504 | 270 | 41.7161
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 20 | 17 | 515.3366 | 0.277 | 142.7482 | 279 | 39.8268
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 20 | 15.9 | 481.9913 | 0.277 | 133.5116 | 279 | 37.2497
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 20 | 15 | 454.7088 | 0.277 | 125.9543 | 270 | 34.0077
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 20 | 14 | 424.3949 | 0.277 | 117.5574 | 279 | 32.7985
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 20 | 11.2 | 339.5159 | 0.277 | 94.0459 | 270 | 25.3924
|  | Tinf for setpoint 20 degrees C | [11 empty] | 210.9911
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 21 | 17.4 | 527.4622 | 0.277 | 146.107 | 270 | 39.4489
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 21 | 16 | 485.0227 | 0.277 | 134.3513 | 279 | 37.484
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 21 | 14.9 | 451.6774 | 0.277 | 125.1146 | 279 | 34.907
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 21 | 14 | 424.3949 | 0.277 | 117.5574 | 270 | 31.7405
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 21 | 13 | 394.081 | 0.277 | 109.1604 | 279 | 30.4558
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 21 | 10.2 | 309.202 | 0.277 | 85.6489 | 270 | 23.1252
|  | Tinf for setpoint 21 degrees C | [11 empty] | 197.1614
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 22 | 16.4 | 497.1483 | 0.277 | 137.7101 | 270 | 37.1817
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 22 | 15 | 454.7088 | 0.277 | 125.9543 | 279 | 35.1413
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 22 | 13.9 | 421.3635 | 0.277 | 116.7177 | 279 | 32.5642
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 22 | 13 | 394.081 | 0.277 | 109.1604 | 270 | 29.4733
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 22 | 12 | 363.767 | 0.277 | 100.7635 | 279 | 28.113
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 22 | 9.2 | 278.8881 | 0.277 | 77.252 | 270 | 20.858
|  | Tinf for setpoint 22 degrees C | [11 empty] | 183.3316
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 23 | 15.4 | 466.8344 | 0.277 | 129.3131 | 270 | 34.9145
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 23 | 14 | 424.3949 | 0.277 | 117.5574 | 279 | 32.7985
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 23 | 12.9 | 391.0496 | 0.277 | 108.3207 | 279 | 30.2215
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 23 | 12 | 363.767 | 0.277 | 100.7635 | 270 | 27.2061
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 23 | 11 | 333.4531 | 0.277 | 92.3665 | 279 | 25.7703
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 23 | 8.2 | 248.5741 | 0.277 | 68.855 | 270 | 18.5909
|  | Tinf for setpoint 23 degrees C | [11 empty] | 169.5018
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 24 | 14.4 | 436.5204 | 0.277 | 120.9162 | 270 | 32.6474
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 24 | 13 | 394.081 | 0.277 | 109.1604 | 279 | 30.4558
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 24 | 11.9 | 360.7356 | 0.277 | 99.9238 | 279 | 27.8787
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 24 | 11 | 333.4531 | 0.277 | 92.3665 | 270 | 24.939
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 24 | 10 | 303.1392 | 0.277 | 83.9696 | 279 | 23.4275
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 24 | 7.2 | 218.2602 | 0.277 | 60.4581 | 270 | 16.3237
|  | Tinf for setpoint 24 degrees C | [11 empty] | 155.672
Total Internal Load by People
|  | Month | People | SenL/person | CLF | SensL (W) | Latent/Person | LatentL (W) | Total peo L (W) | AC opn hrs |  | Total PL (KWh)
|  | Jun | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 270 |  | 113.4
|  | Jul | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 279 |  | 117.18
|  | Aug | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 279 |  | 117.18
|  | Sep | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 270 |  | 113.4
|  | Oct | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 279 |  | 117.18
|  | Nov | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 270 |  | 113.4
|  | Total Internal Load by People | [9 empty] | 691.74
Total Internal Heat Load of Lights per Year
|  | No. Bulbs | Watt Rating | bf | Fu | CLF | hrs (6hrs/day) | Tihlig(KWh)
|  | 3 | 60 | 1.24 | 0.66 | 0.8 | 1098 | 129.3989
|  | Total Internal Heat Load of Lights per Year | [5 empty] | 129.3989
Total Internal Heat Load-Equipment
|  | TV Rating W | Hrs /day | Total hrs | Tihe (KWh)
|  | 36 | 5 | 915 | 32.94
|  | Total load Equipment |  |  | 32.94
Summary of All Other Loads for Chennai
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 18 | 100.7048 | 82.1423 | 238.6507 | 691.74 | 129.3989 | 32.94 | 1275.5767
|  | 19 | 92.7004 | 82.1423 | 224.8209 | 691.74 | 129.3989 | 32.94 | 1253.7425
|  | 20 | 84.6959 | 82.1423 | 210.9911 | 691.74 | 129.3989 | 32.94 | 1231.9083
|  | 21 | 76.6915 | 82.1423 | 197.1614 | 691.74 | 129.3989 | 32.94 | 1210.0741
|  | 22 | 68.6871 | 82.1423 | 183.3316 | 691.74 | 129.3989 | 32.94 | 1188.2399
|  | 23 | 60.8686 | 82.1423 | 169.5018 | 691.74 | 129.3989 | 32.94 | 1166.5916
|  | 24 | 52.8204 | 82.1423 | 155.672 | 691.74 | 129.3989 | 32.94 | 1144.7136
Thermal Conductive Load (TLgw-x) Calculated for Ahmedabad (Hot and Dry)
|  | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 18 | 7.5 | 7.6 | 18.1 | 3.75 | 1.296 | 270 | 23.7508
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 18 | 7.5 | 4.4 | 14.9 | 3.75 | 1.296 | 279 | 20.2035
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 18 | 7.5 | 1.8 | 12.3 | 3.75 | 1.296 | 279 | 16.6781
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 18 | 7.5 | 2.9 | 13.4 | 3.75 | 1.296 | 270 | 17.5835
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 18 | 7.5 | 2 | 12.5 | 3.75 | 1.296 | 279 | 16.9492
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 18 | 7.5 | -1.95 | 8.55 | 3.75 | 1.296 | 270 | 11.2193
|  | TLgw-AMD (KWh)-18 Deg | [12 empty] | 106.3844
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 19 | 6.5 | 7.6 | 17.1 | 3.75 | 1.296 | 270 | 22.4386
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 19 | 6.5 | 4.4 | 13.9 | 3.75 | 1.296 | 279 | 18.8476
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 19 | 6.5 | 1.8 | 11.3 | 3.75 | 1.296 | 279 | 15.3221
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 19 | 6.5 | 2.9 | 12.4 | 3.75 | 1.296 | 270 | 16.2713
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 19 | 6.5 | 2 | 11.5 | 3.75 | 1.296 | 279 | 15.5933
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 19 | 6.5 | -1.95 | 7.55 | 3.75 | 1.296 | 270 | 9.9071
|  | TLgw-AMD (KWh)-19 Deg | [12 empty] | 98.38
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 20 | 5.5 | 7.6 | 16.1 | 3.75 | 1.296 | 270 | 21.1264
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 20 | 5.5 | 4.4 | 12.9 | 3.75 | 1.296 | 279 | 17.4916
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 20 | 5.5 | 1.8 | 10.3 | 3.75 | 1.296 | 279 | 13.9662
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 20 | 5.5 | 2.9 | 11.4 | 3.75 | 1.296 | 270 | 14.9591
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 20 | 5.5 | 2 | 10.5 | 3.75 | 1.296 | 279 | 14.2374
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 20 | 5.5 | -1.95 | 6.55 | 3.75 | 1.296 | 270 | 8.5949
|  | TLgw-AMD (KWh)-20 Deg | [12 empty] | 90.3756
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 21 | 4.5 | 7.6 | 15.1 | 3.75 | 1.296 | 270 | 19.8142
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 21 | 4.5 | 4.4 | 11.9 | 3.75 | 1.296 | 279 | 16.1357
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 21 | 4.5 | 1.8 | 9.3 | 3.75 | 1.296 | 279 | 12.6102
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 21 | 4.5 | 2.9 | 10.4 | 3.75 | 1.296 | 270 | 13.6469
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 21 | 4.5 | 2 | 9.5 | 3.75 | 1.296 | 279 | 12.8814
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 21 | 4.5 | -1.95 | 5.55 | 3.75 | 1.296 | 270 | 7.2827
|  | TLgw-AMD (KWh)-21 Deg | [12 empty] | 82.3712
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 22 | 3.5 | 7.6 | 14.1 | 3.75 | 1.296 | 270 | 18.502
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 22 | 3.5 | 4.4 | 10.9 | 3.75 | 1.296 | 279 | 14.7797
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 22 | 3.5 | 1.8 | 8.3 | 3.75 | 1.296 | 279 | 11.2543
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 22 | 3.5 | 2.9 | 9.4 | 3.75 | 1.296 | 270 | 12.3347
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 22 | 3.5 | 2 | 8.5 | 3.75 | 1.296 | 279 | 11.5255
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 22 | 3.5 | -1.95 | 4.55 | 3.75 | 1.296 | 270 | 5.9705
|  | TLgw-AMD (KWh)-22 Deg | [12 empty] | 74.3667
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 23 | 2.5 | 7.6 | 13.1 | 3.75 | 1.296 | 270 | 17.1898
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 23 | 2.5 | 4.4 | 9.9 | 3.75 | 1.296 | 279 | 13.4238
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 23 | 2.5 | 1.8 | 7.3 | 3.75 | 1.296 | 279 | 9.8984
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 23 | 2.5 | 2.9 | 8.4 | 3.75 | 1.296 | 270 | 11.0225
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 23 | 2.5 | 2 | 7.5 | 3.75 | 1.296 | 279 | 10.1696
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 23 | 2.5 | -1.95 | 3.55 | 3.75 | 1.296 | 270 | 4.6583
|  | TLgw-AMD (KWh)-23 Deg | [12 empty] | 66.3623
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 24 | 1.5 | 7.6 | 12.1 | 3.75 | 1.296 | 270 | 15.8776
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 24 | 1.5 | 4.4 | 8.9 | 3.75 | 1.296 | 279 | 12.0679
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 24 | 1.5 | 1.8 | 6.3 | 3.75 | 1.296 | 279 | 8.5424
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 24 | 1.5 | 2.9 | 7.4 | 3.75 | 1.296 | 270 | 9.7103
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 24 | 1.5 | 2 | 6.5 | 3.75 | 1.296 | 279 | 8.8136
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 24 | 1.5 | -1.95 | 2.55 | 3.75 | 1.296 | 270 | 3.3461
|  | TLgw-AMD (KWh)-24 Deg | [12 empty] | 58.3579
Annual Radiation Thermal Load Through Glass Window- Ahmedabad
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jun | 0.55 | 0.51 | 173.5 | 1.296 | 270 | 17.0295
|  | Jul | 0.55 | 0.51 | 141.95 | 1.296 | 279 | 14.3972
|  | Aug | 0.55 | 0.51 | 119.87 | 1.296 | 279 | 12.1577
|  | Sep | 0.55 | 0.51 | 110.41 | 1.296 | 270 | 10.837
|  | Oct | 0.55 | 0.51 | 97.79 | 1.296 | 279 | 9.9183
|  | Nov | 0.55 | 0.51 | 85.17 | 1.296 | 270 | 8.3597
|  | Tlrad-AMD | [5 empty] | 72.6993
Inflitration Load for Different Setpoint Temperatures for Ahmedabad
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 18 | 23.9 | 724.5027 | 0.277 | 200.6872 | 270 | 54.1856
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 18 | 18.9 | 572.9331 | 0.277 | 158.7025 | 279 | 44.278
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 18 | 16.1 | 488.0541 | 0.277 | 135.191 | 279 | 37.7183
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 18 | 18.1 | 548.6819 | 0.277 | 151.9849 | 270 | 41.0359
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 18 | 19.8 | 600.2156 | 0.277 | 166.2597 | 279 | 46.3865
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 18 | 16.8 | 509.2738 | 0.277 | 141.0689 | 270 | 38.0886
|  | Tinf for setpoint 18 degrees C | [11 empty] | 261.6928
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 19 | 22.9 | 694.1888 | 0.277 | 192.2903 | 270 | 51.9184
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 19 | 17.9 | 542.6192 | 0.277 | 150.3055 | 279 | 41.9352
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 19 | 15.1 | 457.7402 | 0.277 | 126.794 | 279 | 35.3755
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 19 | 17.1 | 518.368 | 0.277 | 143.5879 | 270 | 38.7687
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 19 | 18.8 | 569.9017 | 0.277 | 157.8628 | 279 | 44.0437
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 19 | 15.8 | 478.9599 | 0.277 | 132.6719 | 270 | 35.8214
|  | Tinf for setpoint 19 degrees C | [11 empty] | 247.863
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 20 | 21.9 | 663.8748 | 0.277 | 183.8933 | 270 | 49.6512
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 20 | 16.9 | 512.3052 | 0.277 | 141.9086 | 279 | 39.5925
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 20 | 14.1 | 427.4263 | 0.277 | 118.3971 | 279 | 33.0328
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 20 | 16.1 | 488.0541 | 0.277 | 135.191 | 270 | 36.5016
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 20 | 17.8 | 539.5878 | 0.277 | 149.4658 | 279 | 41.701
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 20 | 14.8 | 448.646 | 0.277 | 124.2749 | 270 | 33.5542
|  | Tinf for setpoint 20 degrees C | [11 empty] | 234.0332
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 21 | 20.9 | 633.5609 | 0.277 | 175.4964 | 270 | 47.384
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 21 | 15.9 | 481.9913 | 0.277 | 133.5116 | 279 | 37.2497
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 21 | 13.1 | 397.1123 | 0.277 | 110.0001 | 279 | 30.69
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 21 | 15.1 | 457.7402 | 0.277 | 126.794 | 270 | 34.2344
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 21 | 16.8 | 509.2738 | 0.277 | 141.0689 | 279 | 39.3582
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 21 | 13.8 | 418.3321 | 0.277 | 115.878 | 270 | 31.2871
|  | Tinf for setpoint 21 degrees C | [11 empty] | 220.2034
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 22 | 19.9 | 603.247 | 0.277 | 167.0994 | 270 | 45.1168
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 22 | 14.9 | 451.6774 | 0.277 | 125.1146 | 279 | 34.907
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 22 | 12.1 | 366.7984 | 0.277 | 101.6032 | 279 | 28.3473
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 22 | 14.1 | 427.4263 | 0.277 | 118.3971 | 270 | 31.9672
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 22 | 15.8 | 478.9599 | 0.277 | 132.6719 | 279 | 37.0155
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 22 | 12.8 | 388.0182 | 0.277 | 107.481 | 270 | 29.0199
|  | Tinf for setpoint 22 degrees C | [11 empty] | 206.3737
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 23 | 18.9 | 572.9331 | 0.277 | 158.7025 | 270 | 42.8497
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 23 | 13.9 | 421.3635 | 0.277 | 116.7177 | 279 | 32.5642
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 23 | 11.1 | 336.4845 | 0.277 | 93.2062 | 279 | 26.0045
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 23 | 13.1 | 397.1123 | 0.277 | 110.0001 | 270 | 29.7
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 23 | 14.8 | 448.646 | 0.277 | 124.2749 | 279 | 34.6727
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 23 | 11.8 | 357.7043 | 0.277 | 99.0841 | 270 | 26.7527
|  | Tinf for setpoint 23 degrees C | [11 empty] | 192.5439
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 24 | 17.9 | 542.6192 | 0.277 | 150.3055 | 270 | 40.5825
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 24 | 12.9 | 391.0496 | 0.277 | 108.3207 | 279 | 30.2215
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 24 | 10.1 | 306.1706 | 0.277 | 84.8093 | 279 | 23.6618
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 24 | 12.1 | 366.7984 | 0.277 | 101.6032 | 270 | 27.4329
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 24 | 13.8 | 418.3321 | 0.277 | 115.878 | 279 | 32.33
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 24 | 10.8 | 327.3903 | 0.277 | 90.6871 | 270 | 24.4855
|  | Tinf for setpoint 24 degrees C | [11 empty] | 178.7141
| 347 | Summary of All Other Loads for Ahmedabad
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 18 | 106.3844 | 72.6993 | 261.6928 | 691.74 | 129.3989 | 32.94 | 1294.8554
|  | 19 | 98.38 | 72.6993 | 247.863 | 691.74 | 129.3989 | 32.94 | 1273.0212
|  | 20 | 90.3756 | 72.6993 | 234.0332 | 691.74 | 129.3989 | 32.94 | 1251.187
|  | 21 | 82.3712 | 72.6993 | 220.2034 | 691.74 | 129.3989 | 32.94 | 1229.3528
|  | 22 | 74.3667 | 72.6993 | 206.3737 | 691.74 | 129.3989 | 32.94 | 1207.5186
|  | 23 | 66.3623 | 72.6993 | 192.5439 | 691.74 | 129.3989 | 32.94 | 1185.6844
|  | 24 | 58.3579 | 72.6993 | 178.7141 | 691.74 | 129.3989 | 32.94 | 1163.8502
Thermal Conductive Load (TLgw-x) Calculated for Delhi (Composite)
|  | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 18 | 5.5 | 9.35 | 17.85 | 3.75 | 1.296 | 270 | 23.4228
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 18 | 5.5 | 6.05 | 14.55 | 3.75 | 1.296 | 279 | 19.7289
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 18 | 7.5 | 4.1 | 14.6 | 3.75 | 1.296 | 279 | 19.7967
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 18 | 7.5 | 3.25 | 13.75 | 3.75 | 1.296 | 270 | 18.0428
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 18 | 7.5 | -0.1 | 10.4 | 3.75 | 1.296 | 279 | 14.1018
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 18 | 7.5 | -5.1 | 5.4 | 3.75 | 1.296 | 270 | 7.0859
|  | TLgw-DEL (KWh)-18 Deg | [12 empty] | 102.1788
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 19 | 5.5 | 9.35 | 17.85 | 3.75 | 1.296 | 270 | 23.4228
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 19 | 5.5 | 6.05 | 14.55 | 3.75 | 1.296 | 279 | 19.7289
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 19 | 6.5 | 4.1 | 13.6 | 3.75 | 1.296 | 279 | 18.4408
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 19 | 6.5 | 3.25 | 12.75 | 3.75 | 1.296 | 270 | 16.7306
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 19 | 6.5 | -0.1 | 9.4 | 3.75 | 1.296 | 279 | 12.7458
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 19 | 6.5 | -5.1 | 4.4 | 3.75 | 1.296 | 270 | 5.7737
|  | TLgw-DEL (KWh)-19 Deg | [12 empty] | 96.8425
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 20 | 5.5 | 9.35 | 17.85 | 3.75 | 1.296 | 270 | 23.4228
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 20 | 5.5 | 6.05 | 14.55 | 3.75 | 1.296 | 279 | 19.7289
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 20 | 5.5 | 4.1 | 12.6 | 3.75 | 1.296 | 279 | 17.0848
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 20 | 5.5 | 3.25 | 11.75 | 3.75 | 1.296 | 270 | 15.4184
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 20 | 5.5 | -0.1 | 8.4 | 3.75 | 1.296 | 279 | 11.3899
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 20 | 5.5 | -5.1 | 3.4 | 3.75 | 1.296 | 270 | 4.4615
|  | TLgw-DEL (KWh)-20 Deg | [12 empty] | 91.5063
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 21 | 4.5 | 9.35 | 16.85 | 3.75 | 1.296 | 270 | 22.1106
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 21 | 4.5 | 6.05 | 13.55 | 3.75 | 1.296 | 279 | 18.373
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 21 | 4.5 | 4.1 | 11.6 | 3.75 | 1.296 | 279 | 15.7289
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 21 | 4.5 | 3.25 | 10.75 | 3.75 | 1.296 | 270 | 14.1062
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 21 | 4.5 | -0.1 | 7.4 | 3.75 | 1.296 | 279 | 10.034
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 21 | 4.5 | -5.1 | 2.4 | 3.75 | 1.296 | 270 | 3.1493
|  | TLgw-DEL (KWh)-21 Deg | [12 empty] | 83.5018
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 22 | 3.5 | 9.35 | 15.85 | 3.75 | 1.296 | 270 | 20.7984
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 22 | 3.5 | 6.05 | 12.55 | 3.75 | 1.296 | 279 | 17.017
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 22 | 3.5 | 4.1 | 10.6 | 3.75 | 1.296 | 279 | 14.373
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 22 | 3.5 | 3.25 | 9.75 | 3.75 | 1.296 | 270 | 12.7939
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 22 | 3.5 | -0.1 | 6.4 | 3.75 | 1.296 | 279 | 8.678
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 22 | 3.5 | -5.1 | 1.4 | 3.75 | 1.296 | 270 | 1.8371
|  | TLgw-DEL (KWh)-22 Deg | [12 empty] | 75.4974
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 23 | 2.5 | 9.35 | 14.85 | 3.75 | 1.296 | 270 | 19.4862
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 23 | 2.5 | 6.05 | 11.55 | 3.75 | 1.296 | 279 | 15.6611
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 23 | 2.5 | 4.1 | 9.6 | 3.75 | 1.296 | 279 | 13.017
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 23 | 2.5 | 3.25 | 8.75 | 3.75 | 1.296 | 270 | 11.4817
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 23 | 2.5 | -0.1 | 5.4 | 3.75 | 1.296 | 279 | 7.3221
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 23 | 2.5 | -5.1 | 0.4 | 3.75 | 1.296 | 270 | 0.52488
|  | TLgw-DEL (KWh)-23 Deg | [12 empty] | 67.493
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 24 | 1.5 | 9.35 | 13.85 | 3.75 | 1.296 | 270 | 18.174
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 24 | 1.5 | 6.05 | 10.55 | 3.75 | 1.296 | 279 | 14.3052
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 24 | 1.5 | 4.1 | 8.6 | 3.75 | 1.296 | 279 | 11.6611
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 24 | 1.5 | 3.25 | 7.75 | 3.75 | 1.296 | 270 | 10.1695
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 24 | 1.5 | -0.1 | 4.4 | 3.75 | 1.296 | 279 | 5.9661
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 24 | 1.5 | -5.1 | -0.6 | 3.75 | 1.296 | 270 | -0.78732
|  | TLgw-DEL (KWh)-24 Deg | [12 empty] | 59.4886
Annual Radiation Thermal Load Through Glass Window- Delhi
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jun | 0.55 | 0.51 | 138.8 | 1.296 | 270 | 13.6236
|  | Jul | 0.55 | 0.51 | 126.18 | 1.296 | 279 | 12.7977
|  | Aug | 0.55 | 0.51 | 116.71 | 1.296 | 279 | 11.8372
|  | Sep | 0.55 | 0.51 | 104.1 | 1.296 | 270 | 10.2177
|  | Oct | 0.55 | 0.51 | 88.32 | 1.296 | 279 | 8.9578
|  | Nov | 0.55 | 0.51 | 75.71 | 1.296 | 270 | 7.4311
|  | Tlrad-AMD | [5 empty] | 64.8651
Inflitration Load for Different Setpoint Temperatures for Delhi
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 18 | 25.8 | 782.0991 | 0.277 | 216.6415 | 270 | 58.4932
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 18 | 21 | 636.5923 | 0.277 | 176.3361 | 279 | 49.1978
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 18 | 18.9 | 572.9331 | 0.277 | 158.7025 | 279 | 44.278
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 18 | 18.8 | 569.9017 | 0.277 | 157.8628 | 270 | 42.6229
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 18 | 17.2 | 521.3994 | 0.277 | 144.4276 | 279 | 40.2953
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 18 | 12.8 | 388.0182 | 0.277 | 107.481 | 270 | 29.0199
|  | Tinf for setpoint 18 degrees C | [11 empty] | 263.9071
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 19 | 24.8 | 751.7852 | 0.277 | 208.2445 | 270 | 56.226
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 19 | 20 | 606.2784 | 0.277 | 167.9391 | 279 | 46.855
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 19 | 17.9 | 542.6192 | 0.277 | 150.3055 | 279 | 41.9352
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 19 | 17.8 | 539.5878 | 0.277 | 149.4658 | 270 | 40.3558
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 19 | 16.2 | 491.0855 | 0.277 | 136.0307 | 279 | 37.9526
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 19 | 11.8 | 357.7043 | 0.277 | 99.0841 | 270 | 26.7527
|  | Tinf for setpoint 19 degrees C | [11 empty] | 250.0773
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 20 | 23.8 | 721.4713 | 0.277 | 199.8475 | 270 | 53.9588
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 20 | 19 | 575.9645 | 0.277 | 159.5422 | 279 | 44.5123
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 20 | 16.9 | 512.3052 | 0.277 | 141.9086 | 279 | 39.5925
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 20 | 16.8 | 509.2738 | 0.277 | 141.0689 | 270 | 38.0886
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 20 | 15.2 | 460.7716 | 0.277 | 127.6337 | 279 | 35.6098
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 20 | 10.8 | 327.3903 | 0.277 | 90.6871 | 270 | 24.4855
|  | Tinf for setpoint 20 degrees C | [11 empty] | 236.2475
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 21 | 22.8 | 691.1574 | 0.277 | 191.4506 | 270 | 51.6917
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 21 | 18 | 545.6506 | 0.277 | 151.1452 | 279 | 42.1695
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 21 | 15.9 | 481.9913 | 0.277 | 133.5116 | 279 | 37.2497
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 21 | 15.8 | 478.9599 | 0.277 | 132.6719 | 270 | 35.8214
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 21 | 14.2 | 430.4577 | 0.277 | 119.2368 | 279 | 33.2671
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 21 | 9.8 | 297.0764 | 0.277 | 82.2902 | 270 | 22.2183
|  | Tinf for setpoint 21 degrees C | [11 empty] | 222.4177
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 22 | 21.8 | 660.8434 | 0.277 | 183.0536 | 270 | 49.4245
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 22 | 17 | 515.3366 | 0.277 | 142.7482 | 279 | 39.8268
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 22 | 14.9 | 451.6774 | 0.277 | 125.1146 | 279 | 34.907
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 22 | 14.8 | 448.646 | 0.277 | 124.2749 | 270 | 33.5542
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 22 | 13.2 | 400.1437 | 0.277 | 110.8398 | 279 | 30.9243
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 22 | 8.8 | 266.7625 | 0.277 | 73.8932 | 270 | 19.9512
|  | Tinf for setpoint 22 degrees C | [11 empty] | 208.5879
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 22 | 21.8 | 660.8434 | 0.277 | 183.0536 | 270 | 49.4245
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 23 | 16 | 485.0227 | 0.277 | 134.3513 | 279 | 37.484
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 23 | 13.9 | 421.3635 | 0.277 | 116.7177 | 279 | 32.5642
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 23 | 13.8 | 418.3321 | 0.277 | 115.878 | 270 | 31.2871
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 23 | 12.2 | 369.8298 | 0.277 | 102.4429 | 279 | 28.5816
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 22 | 8.8 | 266.7625 | 0.277 | 73.8932 | 270 | 19.9512
|  | Tinf for setpoint 23 degrees C | [11 empty] | 199.2925
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 22 | 21.8 | 660.8434 | 0.277 | 183.0536 | 270 | 49.4245
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 24 | 15 | 454.7088 | 0.277 | 125.9543 | 279 | 35.1413
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 24 | 12.9 | 391.0496 | 0.277 | 108.3207 | 279 | 30.2215
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 24 | 12.8 | 388.0182 | 0.277 | 107.481 | 270 | 29.0199
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 24 | 11.2 | 339.5159 | 0.277 | 94.0459 | 279 | 26.2388
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 22 | 8.8 | 266.7625 | 0.277 | 73.8932 | 270 | 19.9512
|  | Tinf for setpoint 24 degrees C | [11 empty] | 189.9971
Summary of All Other Loads for Delhi
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 18 | 102.1788 | 64.8651 | 263.9071 | 691.74 | 129.3989 | 32.94 | 1285.0299
|  | 19 | 96.8425 | 64.8651 | 250.0773 | 691.74 | 129.3989 | 32.94 | 1265.8638
|  | 20 | 91.5063 | 64.8651 | 236.2475 | 691.74 | 129.3989 | 32.94 | 1246.6978
|  | 21 | 83.5018 | 64.8651 | 222.4177 | 691.74 | 129.3989 | 32.94 | 1224.8636
|  | 22 | 75.4974 | 64.8651 | 208.5879 | 691.74 | 129.3989 | 32.94 | 1203.0294
|  | 23 | 67.493 | 64.8651 | 199.2925 | 691.74 | 129.3989 | 32.94 | 1185.7295
|  | 24 | 59.4886 | 64.8651 | 189.9971 | 691.74 | 129.3989 | 32.94 | 1168.4297

## India Dengue Season igr
Balance Point Temperature, Annual Variable Degree Days, Thermal Load of Living Space and Annual Electricity Consumption Calculations for No Insulation (Indian Electrical Grid Mix and Solar Electricity) for Baseline Scenario (Low Dengue Risk AC Temperature Zone (22-25°C) for all Three Climate Scenarios in India
|  | Chennai (Warm and Humid Climate) | [31 empty] | LDRZ Use Temperature Setpoint Preference %
|  | Month | [7 empty] | Tbal-m calc | Tbal-m used | VCDDmth | AC hrs/24 hrs (fAC) | Conv (24/1000) KWh |  |  | Annual VCDD | TLBE-r-x |  |  | Annual VCDD | TLBE-f-x |  |  | Annual VCDD | TLBE-wallop-x | All Other Heat Loads | BE+Other Loads | 10%SF | TATL-x | EER | AC Setpt- Elec Cons (KWh) | Avg Elec Cons (KWh) | AC Setpoint Temp (°C) | % Preference | Adj. Pref %
|  | Jun | 18 | 75.6865 | 420 | 118.8 | 36 | 25.16 | 8.47 | -1.3424 | -1.5 | 1005.5 | [21 empty] | 18 | 6 | 0.09375
|  | Jul | 18 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.96735 | -1 | 1005.1 | [21 empty] | 19 | 1 | 0.015625
|  | Aug | 18 | 47.0151 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.48989 | -0.5 | 958.5 | [21 empty] | 20 | 7 | 0.10938
|  | Sep | 18 | 41.2822 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.31942 | -0.5 | 933.1 | [21 empty] | 21 | 4 | 0.0625
|  | Oct | 18 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.21717 | 0 | 911.7 | [21 empty] | 22 | 16 | 0.25
|  | Nov | 18 | 34.4007 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.1148 | 0 | 822.8 | [21 empty] | 23 | 10 | 0.15625
|  | VCDD-18 Deg | [9 empty] | 5636.7 | 0.375 | 0.024 | 0.276 | 12.96 | 5636.7 | 181.4603 | 0.278 | 12.96 | 5636.7 | 182.7752 | 0.42 | 41.904 | 5636.7 | 892.837 | 1237.9803 | 2495.0527 | 249.5053 | 2744.558 | 3.1 | 885 |  | 24 | 20 | 0.3125
|  | Jun | 19 | 75.6865 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.34245 | -0.5 | 975.5 | [22 empty] | 64
|  | Jul | 19 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.032646 | 0 | 974.1
|  | Aug | 19 | 47.0151 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.51011 | 0.5 | 927.5
|  | Sep | 19 | 41.2822 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.68058 | 0.5 | 903.1
|  | Oct | 19 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.78283 | 1 | 880.7
|  | Nov | 19 | 34.4007 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.8852 | 1 | 792.8
|  | VCDD-19 Deg | [9 empty] | 5453.7 | 0.375 | 0.024 | 0.276 | 12.96 | 5453.7 | 175.569 | 0.278 | 12.96 | 5453.7 | 176.8412 | 0.42 | 41.904 | 5453.7 | 863.8504 | 1219.1344 | 2435.395 | 243.5395 | 2678.9345 | 3.1 | 864
|  | Jun | 20 | 75.6865 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.65755 | 0.5 | 945.5
|  | Jul | 20 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.0326 | 1 | 943.1
|  | Aug | 20 | 47.0151 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.5101 | 1.5 | 896.5
|  | Sep | 20 | 41.2822 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.6806 | 1.5 | 873.1
|  | Oct | 20 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.7828 | 2 | 849.7
|  | Nov | 20 | 34.4007 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.8852 | 2 | 762.8
|  | VCDD-20 Deg | [9 empty] | 5270.7 | 0.375 | 0.024 | 0.276 | 12.96 | 5270.7 | 169.6777 | 0.278 | 12.96 | 5270.7 | 170.9073 | 0.42 | 41.904 | 5270.7 | 834.8637 | 1200.2885 | 2375.7372 | 237.5737 | 2613.3109 | 3.1 | 843
|  | Jun | 21 | 75.6865 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.6576 | 1.5 | 915.5
|  | Jul | 21 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.0326 | 2 | 912.1
|  | Aug | 21 | 47.0151 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.5101 | 2.5 | 865.5
|  | Sep | 21 | 41.2822 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.6806 | 2.5 | 843.1
|  | Oct | 21 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.7828 | 3 | 818.7
|  | Nov | 21 | 34.4007 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.8852 | 3 | 732.8
|  | VCDD-21 Deg | [9 empty] | 5087.7 | 0.375 | 0.024 | 0.276 | 12.96 | 5087.7 | 163.7865 | 0.278 | 12.96 | 5087.7 | 164.9734 | 0.42 | 41.904 | 5087.7 | 805.877 | 1181.4426 | 2316.0795 | 231.6079 | 2547.6874 | 3.1 | 822
|  | Jun | 22 | 75.6865 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.6576 | 2.5 | 885.5
|  | Jul | 22 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.0326 | 3 | 881.1
|  | Aug | 22 | 47.0151 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.5101 | 3.5 | 834.5
|  | Sep | 22 | 41.2822 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.6806 | 3.5 | 813.1
|  | Oct | 22 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.7828 | 4 | 787.7
|  | Nov | 22 | 34.4007 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.8852 | 4 | 702.8
|  | VCDD-22 Deg | [9 empty] | 4904.7 | 0.375 | 0.024 | 0.276 | 12.96 | 4904.7 | 157.8952 | 0.278 | 12.96 | 4904.7 | 159.0394 | 0.42 | 41.904 | 4904.7 | 776.8904 | 1162.5967 | 2256.4217 | 225.6422 | 2482.0639 | 3.1 | 801
|  | Jun | 23 | 75.6865 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.6576 | 3.5 | 855.5
|  | Jul | 23 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.0326 | 4 | 850.1
|  | Aug | 23 | 47.0151 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.5101 | 4.5 | 803.5
|  | Sep | 23 | 41.2822 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.6806 | 4.5 | 783.1
|  | Oct | 23 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.7828 | 5 | 756.7
|  | Nov | 23 | 34.4007 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.8852 | 5 | 672.8
|  | VCDD-23 Deg | [9 empty] | 4721.7 | 0.375 | 0.024 | 0.276 | 12.96 | 4721.7 | 152.004 | 0.278 | 12.96 | 4721.7 | 153.1055 | 0.42 | 41.904 | 4721.7 | 747.9037 | 1144.1441 | 2197.1573 | 219.7157 | 2416.873 | 3.1 | 780
|  | Jun | 24 | 75.6865 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.6576 | 4.5 | 825.5
|  | Jul | 24 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.0326 | 5 | 819.1
|  | Aug | 24 | 47.0151 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.5101 | 5.5 | 772.5
|  | Sep | 24 | 41.2822 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.6806 | 5.5 | 753.1
|  | Oct | 24 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.7828 | 6 | 725.7
|  | Nov | 24 | 34.4007 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.8852 | 6 | 642.8
|  | VCDD-24 Deg | [9 empty] | 4538.7 | 0.375 | 0.024 | 0.276 | 12.96 | 4538.7 | 146.1127 | 0.278 | 12.96 | 4538.7 | 147.1715 | 0.42 | 41.904 | 4538.7 | 718.917 | 1125.2434 | 2137.4447 | 213.7445 | 2351.1892 | 3.1 | 758
|  | Total Energy Consumption for Operation of AC Unit Between Setpoint Temperature of 18-24°C (Based on User Setpoint Preferences) for Chennai (Warm and Humid) for ECBC Scenario | [30 empty] | 799
Ahmedabad (Hot and Dry)
|  | Month | [7 empty] | Tbal-m calc | Tbal-m used | VCDDmth
|  | Jun | 18 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.96735 | -1 | 916.9
|  | Jul | 18 | 51.6028 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.62631 | -0.5 | 875
|  | Aug | 18 | 43.5761 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.38763 | -0.5 | 874.2
|  | Sep | 18 | 40.1371 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.28537 | -0.5 | 856.5
|  | Oct | 18 | 35.5494 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.14896 | 0 | 902.2
|  | Nov | 18 | 30.9617 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.012539 | 0 | 757
|  | VCDD-18 Deg | [9 empty] | 5181.8 | 0.375 | 0.024 | 0.276 | 12.96 | 5181.8 | 166.8158 | 0.278 | 12.96 | 5181.8 | 168.0246 | 0.42 | 41.904 | 5181.8 | 820.7822 | 1255.1386 | 2410.7612 | 241.0761 | 2651.8374 | 3.1 | 855
|  | Jun | 19 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.032646 | 0 | 886.9
|  | Jul | 19 | 51.6028 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.37369 | 0.5 | 844
|  | Aug | 19 | 43.5761 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.61237 | 0.5 | 843.2
|  | Sep | 19 | 40.1371 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.71463 | 0.5 | 826.5
|  | Oct | 19 | 35.5494 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.85104 | 1 | 871.2
|  | Nov | 19 | 30.9617 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.98746 | 1 | 727
|  | VCDD-19 Deg | [9 empty] | 4998.8 | 0.375 | 0.024 | 0.276 | 12.96 | 4998.8 | 160.9246 | 0.278 | 12.96 | 4998.8 | 162.0907 | 0.42 | 41.904 | 4998.8 | 791.7955 | 1236.2927 | 2351.1035 | 235.1103 | 2586.2138 | 3.1 | 834
|  | Jun | 20 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.0326 | 1 | 828.5
|  | Jul | 20 | 51.6028 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.3737 | 1.5 | 813
|  | Aug | 20 | 43.5761 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.6124 | 1.5 | 812.2
|  | Sep | 20 | 40.1371 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.7146 | 1.5 | 796.5
|  | Oct | 20 | 35.5494 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.851 | 2 | 840.2
|  | Nov | 20 | 30.9617 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.9875 | 2 | 697
|  | VCDD-20 Deg | [9 empty] | 4787.4 | 0.375 | 0.024 | 0.276 | 12.96 | 4787.4 | 154.119 | 0.278 | 12.96 | 4787.4 | 155.2358 | 0.42 | 41.904 | 4787.4 | 758.3104 | 1217.4468 | 2285.1121 | 228.5112 | 2513.6233 | 3.1 | 811
|  | Jun | 21 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.0326 | 2 | 826.9
|  | Jul | 21 | 51.6028 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.3737 | 2.5 | 782
|  | Aug | 21 | 43.5761 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.6124 | 2.5 | 781.2
|  | Sep | 21 | 40.1371 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.7146 | 2.5 | 766.5
|  | Oct | 21 | 35.5494 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.851 | 3 | 809.2
|  | Nov | 21 | 30.9617 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.9875 | 3 | 667
|  | VCDD-21 Deg | [9 empty] | 4632.8 | 0.375 | 0.024 | 0.276 | 12.96 | 4632.8 | 149.1421 | 0.278 | 12.96 | 4632.8 | 150.2228 | 0.42 | 41.904 | 4632.8 | 733.8222 | 1198.6009 | 2231.788 | 223.1788 | 2454.9668 | 3.1 | 792
|  | Jun | 22 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.0326 | 3 | 796.9
|  | Jul | 22 | 51.6028 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.3737 | 3.5 | 751
|  | Aug | 22 | 43.5761 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.6124 | 3.5 | 750.2
|  | Sep | 22 | 40.1371 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.7146 | 3.5 | 736.5
|  | Oct | 22 | 35.5494 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.851 | 4 | 778.2
|  | Nov | 22 | 30.9617 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.9875 | 4 | 637
|  | VCDD-22 Deg | [9 empty] | 4449.8 | 0.375 | 0.024 | 0.276 | 12.96 | 4449.8 | 143.2508 | 0.278 | 12.96 | 4449.8 | 144.2889 | 0.42 | 41.904 | 4449.8 | 704.8355 | 1179.755 | 2172.1302 | 217.213 | 2389.3432 | 3.1 | 771
|  | Jun | 23 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.0326 | 4 | 766.9
|  | Jul | 23 | 51.6028 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.3737 | 4.5 | 720
|  | Aug | 23 | 43.5761 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.6124 | 4.5 | 719.2
|  | Sep | 23 | 40.1371 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.7146 | 4.5 | 706.5
|  | Oct | 23 | 35.5494 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.851 | 5 | 747.2
|  | Nov | 23 | 30.9617 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.9875 | 5 | 607
|  | VCDD-23 Deg | [9 empty] | 4266.8 | 0.375 | 0.024 | 0.276 | 12.96 | 4266.8 | 137.3596 | 0.278 | 12.96 | 4266.8 | 138.3549 | 0.42 | 41.904 | 4266.8 | 675.8488 | 1160.9091 | 2112.4724 | 211.2472 | 2323.7197 | 3.1 | 750
|  | Jun | 24 | 63.0721 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.0326 | 5 | 736.9
|  | Jul | 24 | 51.6028 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.3737 | 5.5 | 689
|  | Aug | 24 | 43.5761 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.6124 | 5.5 | 688.2
|  | Sep | 24 | 40.1371 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.7146 | 5.5 | 676.5
|  | Oct | 24 | 35.5494 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.851 | 6 | 716.2
|  | Nov | 24 | 30.9617 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.9875 | 6 | 577
|  | VCDD-24 Deg | [9 empty] | 4083.8 | 0.375 | 0.024 | 0.276 | 12.96 | 4083.8 | 131.4683 | 0.278 | 12.96 | 4083.8 | 132.421 | 0.42 | 41.904 | 4083.8 | 646.8622 | 1142.0632 | 2052.8147 | 205.2815 | 2258.0962 | 3.1 | 728
|  | Total Energy Consumption for Operation of AC Unit Between Setpoint Temperature of 18-24°C (Based on User Setpoint Preferences) for Ahmedabad (Hot and Dry) for ECBC Scenario | [30 empty] | 769
Delhi (Composite)
|  | Month | [7 empty] | Tbal-m calc | Tbal-m used | VCDDmth
|  | Jun | 18 | 50.4577 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.59226 | -0.5 | 980.9
|  | Jul | 18 | 45.87 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.45584 | -0.5 | 950.8
|  | Aug | 18 | 42.4274 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.35347 | -0.5 | 939.1
|  | Sep | 18 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.21717 | 0 | 870.9
|  | Oct | 18 | 32.1068 | 420 | 118.8 | 36 | 25.16 | 8.47 | -0.046589 | 0 | 847.9
|  | Nov | 18 | 27.5227 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.08972 | 0 | 621.6
|  | VCDD-18 Deg | [9 empty] | 5211.2 | 0.375 | 0.024 | 0.276 | 12.96 | 5211.2 | 167.7623 | 0.278 | 12.96 | 5211.2 | 168.978 | 0.42 | 41.904 | 5211.2 | 825.4391 | 1162.7141 | 2324.8934 | 232.4893 | 2557.3828 | 3.1 | 825
|  | Jun | 19 | 50.4577 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.40774 | 0.5 | 950.9
|  | Jul | 19 | 45.87 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.54416 | 0.5 | 919.8
|  | Aug | 19 | 42.4274 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.64653 | 0.5 | 908.1
|  | Sep | 19 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.78283 | 1 | 840.9
|  | Oct | 19 | 32.1068 | 420 | 118.8 | 36 | 25.16 | 8.47 | 0.95341 | 1 | 816.9
|  | Nov | 19 | 27.5227 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.0897 | 1 | 591.6
|  | VCDD-19Deg | [9 empty] | 5028.2 | 0.375 | 0.024 | 0.276 | 12.96 | 5028.2 | 161.871 | 0.278 | 12.96 | 5028.2 | 163.044 | 0.42 | 41.904 | 5028.2 | 796.4524 | 1148.4026 | 2269.77 | 226.977 | 2496.7471 | 3.1 | 805
|  | Jun | 20 | 50.4577 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.4077 | 1.5 | 920.9
|  | Jul | 20 | 45.87 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.5442 | 1.5 | 888.8
|  | Aug | 20 | 42.4274 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.6465 | 1.5 | 877.1
|  | Sep | 20 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.7828 | 2 | 810.9
|  | Oct | 20 | 32.1068 | 420 | 118.8 | 36 | 25.16 | 8.47 | 1.9534 | 2 | 785.9
|  | Nov | 20 | 27.5227 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.0897 | 2 | 561.6
|  | VCDD-20 Deg | [9 empty] | 4845.2 | 0.375 | 0.024 | 0.276 | 12.96 | 4845.2 | 155.9798 | 0.278 | 12.96 | 4845.2 | 157.1101 | 0.42 | 41.904 | 4845.2 | 767.4657 | 1134.0911 | 2214.6466 | 221.4647 | 2436.1113 | 3.1 | 786
|  | Jun | 21 | 50.4577 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.4077 | 2.5 | 890.9
|  | Jul | 21 | 45.87 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.5442 | 2.5 | 857.8
|  | Aug | 21 | 42.4274 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.6465 | 2.5 | 846.1
|  | Sep | 21 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.7828 | 3 | 780.9
|  | Oct | 21 | 32.1068 | 420 | 118.8 | 36 | 25.16 | 8.47 | 2.9534 | 3 | 754.9
|  | Nov | 21 | 27.5227 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.0897 | 3 | 531.6
|  | VCDD-21 Deg | [9 empty] | 4662.2 | 0.375 | 0.024 | 0.276 | 12.96 | 4662.2 | 150.0885 | 0.278 | 12.96 | 4662.2 | 151.1761 | 0.42 | 41.904 | 4662.2 | 738.4791 | 1119.7795 | 2159.5232 | 215.9523 | 2375.4756 | 3.1 | 766
|  | Jun | 22 | 50.4577 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.4077 | 3.5 | 860.9
|  | Jul | 22 | 45.87 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.5442 | 3.5 | 826.8
|  | Aug | 22 | 42.4274 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.6465 | 3.5 | 815.1
|  | Sep | 22 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.7828 | 4 | 750.9
|  | Oct | 22 | 32.1068 | 420 | 118.8 | 36 | 25.16 | 8.47 | 3.9534 | 4 | 723.9
|  | Nov | 22 | 27.5227 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.0897 | 4 | 501.6
|  | VCDD-22 Deg | [9 empty] | 4479.2 | 0.375 | 0.024 | 0.276 | 12.96 | 4479.2 | 144.1973 | 0.278 | 12.96 | 4479.2 | 145.2422 | 0.42 | 41.904 | 4479.2 | 709.4924 | 1105.468 | 2104.3998 | 210.44 | 2314.8398 | 3.1 | 747
|  | Jun | 23 | 50.4577 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.4077 | 4.5 | 830.9
|  | Jul | 23 | 45.87 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.5442 | 4.5 | 795.8
|  | Aug | 23 | 42.4274 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.6465 | 4.5 | 784.1
|  | Sep | 23 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.7828 | 5 | 720.9
|  | Oct | 23 | 32.1068 | 420 | 118.8 | 36 | 25.16 | 8.47 | 4.9534 | 5 | 692.9
|  | Nov | 23 | 27.5227 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.0897 | 5 | 471.6
|  | VCDD-23 Deg | [9 empty] | 4296.2 | 0.375 | 0.024 | 0.276 | 12.96 | 4296.2 | 138.306 | 0.278 | 12.96 | 4296.2 | 139.3082 | 0.42 | 41.904 | 4296.2 | 680.5057 | 1091.1565 | 2049.2764 | 204.9276 | 2254.2041 | 3.1 | 727
|  | Jun | 24 | 50.4577 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.4077 | 5.5 | 800.9
|  | Jul | 24 | 45.87 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.5442 | 5.5 | 764.8 | [15 empty] | T
|  | Aug | 24 | 42.4274 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.6465 | 5.5 | 753.1
|  | Sep | 24 | 37.8433 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.7828 | 6 | 690.9 |  | 0
|  | Oct | 24 | 32.1068 | 420 | 118.8 | 36 | 25.16 | 8.47 | 5.9534 | 6 | 661.9
|  | Nov | 24 | 27.5227 | 420 | 118.8 | 36 | 25.16 | 8.47 | 6.0897 | 6 | 441.6
|  | VCDD-24 Deg | [9 empty] | 4113.2 | 0.375 | 0.024 | 0.276 | 12.96 | 4113.2 | 132.4148 | 0.278 | 12.96 | 4113.2 | 133.3743 | 0.42 | 41.904 | 4113.2 | 651.519 | 1076.8449 | 1994.153 | 199.4153 | 2193.5683 | 3.1 | 708
|  | Total Energy Consumption for Operation of AC Unit Between Setpoint Temperature of 18-24°C (Based on User Setpoint Preferences) for Delhi (Composite) for ECBC Scenario | [30 empty] | 745
CLTDgw-avg (°C) for AC Opn hrs. |  | Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 22°C
06.00-07.00 | -1 | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
07.00-08.00 | -1 | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 18 | 7.5 | 4.6 | 15.1 | 2.35 | 1.296 | 270 | 12.4169
08.00-09.00 | 0 | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 18 | 7.5 | 3.55 | 14.05 | 2.35 | 1.296 | 279 | 11.9386
17.00-18.00 | 7 | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 18 | 7.5 | 2.55 | 13.05 | 2.35 | 1.296 | 279 | 11.0889
18.00-19.00 | 7 | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 18 | 7.5 | 1.75 | 12.25 | 2.35 | 1.296 | 270 | 10.0733
19.00-20.00 | 6 | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 18 | 7.5 | 1.25 | 11.75 | 2.35 | 1.296 | 279 | 9.9842
20.00-21.00 | 4 | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 18 | 7.5 | -1.25 | 9.25 | 2.35 | 1.296 | 270 | 7.6064
21.00-22.00 | 3 | TLgw-CHN (KWh)-18 Deg | [12 empty] | 63.1083
22.00-23.00 | 2 | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 19 | 6.5 | 4.6 | 14.1 | 2.35 | 1.296 | 270 | 11.5946
CLTDgw-avg (°C) | 3 | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 19 | 6.5 | 3.55 | 13.05 | 2.35 | 1.296 | 279 | 11.0889
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 19 | 6.5 | 2.55 | 12.05 | 2.35 | 1.296 | 279 | 10.2392
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 19 | 6.5 | 1.75 | 11.25 | 2.35 | 1.296 | 270 | 9.251
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 19 | 6.5 | 1.25 | 10.75 | 2.35 | 1.296 | 279 | 9.1345
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 19 | 6.5 | -1.25 | 8.25 | 2.35 | 1.296 | 270 | 6.7841
|  | TLgw-CHN (KWh)-19 Deg | [12 empty] | 58.0922
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 20 | 5.5 | 4.6 | 13.1 | 2.35 | 1.296 | 270 | 10.7723
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 20 | 5.5 | 3.55 | 12.05 | 2.35 | 1.296 | 279 | 10.2392
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 20 | 5.5 | 2.55 | 11.05 | 2.35 | 1.296 | 279 | 9.3894
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 20 | 5.5 | 1.75 | 10.25 | 2.35 | 1.296 | 270 | 8.4287
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 20 | 5.5 | 1.25 | 9.75 | 2.35 | 1.296 | 279 | 8.2848
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 20 | 5.5 | -1.25 | 7.25 | 2.35 | 1.296 | 270 | 5.9618
|  | TLgw-CHN (KWh)-20 Deg | [12 empty] | 53.0761
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 21 | 4.5 | 4.6 | 12.1 | 2.35 | 1.296 | 270 | 9.95
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 21 | 4.5 | 3.55 | 11.05 | 2.35 | 1.296 | 279 | 9.3894
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 21 | 4.5 | 2.55 | 10.05 | 2.35 | 1.296 | 279 | 8.5397
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 21 | 4.5 | 1.75 | 9.25 | 2.35 | 1.296 | 270 | 7.6064
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 21 | 4.5 | 1.25 | 8.75 | 2.35 | 1.296 | 279 | 7.4351
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 21 | 4.5 | -1.25 | 6.25 | 2.35 | 1.296 | 270 | 5.1395
|  | TLgw-CHN (KWh)-21 Deg | [12 empty] | 48.06
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 22 | 3.5 | 4.6 | 11.1 | 2.35 | 1.296 | 270 | 9.1277
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 22 | 3.5 | 3.55 | 10.05 | 2.35 | 1.296 | 279 | 8.5397
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 22 | 3.5 | 2.55 | 9.05 | 2.35 | 1.296 | 279 | 7.69
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 22 | 3.5 | 1.75 | 8.25 | 2.35 | 1.296 | 270 | 6.7841
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 22 | 3.5 | 1.25 | 7.75 | 2.35 | 1.296 | 279 | 6.5853
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 22 | 3.5 | -1.25 | 5.25 | 2.35 | 1.296 | 270 | 4.3171
|  | TLgw-CHN (KWh)-22 Deg | [12 empty] | 43.0439
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 23 | 2.5 | 4.6 | 10.1 | 2.35 | 1.296 | 279 | 8.5822
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 23 | 2.5 | 3.55 | 9.05 | 2.35 | 1.296 | 279 | 7.69
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 23 | 2.5 | 2.55 | 8.05 | 2.35 | 1.296 | 279 | 6.8403
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 23 | 2.5 | 1.75 | 7.25 | 2.35 | 1.296 | 270 | 5.9618
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 23 | 2.5 | 1.25 | 6.75 | 2.35 | 1.296 | 279 | 5.7356
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 23 | 2.5 | -1.25 | 4.25 | 2.35 | 1.296 | 279 | 3.6113
|  | TLgw-CHN (KWh)-23 Deg | [12 empty] | 38.4212
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 3 | 24 | 1.5 | 4.6 | 9.1 | 2.35 | 1.296 | 279 | 7.7325
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 3 | 24 | 1.5 | 3.55 | 8.05 | 2.35 | 1.296 | 279 | 6.8403
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 3 | 24 | 1.5 | 2.55 | 7.05 | 2.35 | 1.296 | 279 | 5.9905
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 3 | 24 | 1.5 | 1.75 | 6.25 | 2.35 | 1.296 | 270 | 5.1395
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 3 | 24 | 1.5 | 1.25 | 5.75 | 2.35 | 1.296 | 279 | 4.8859
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 3 | 24 | 1.5 | -1.25 | 3.25 | 2.35 | 1.296 | 279 | 2.7616
|  | TLgw-CHN (KWh)-24 Deg | [12 empty] | 33.3502
Annual Radiation Thermal Load Through Glass Window- Chennai
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jun | 0.55 | 0.51 | 208.2 | 1.296 | 270 | 20.4354
|  | Jul | 0.55 | 0.51 | 173.5 | 1.296 | 279 | 17.5971
|  | Aug | 0.55 | 0.51 | 129.33 | 1.296 | 279 | 13.1172
|  | Sep | 0.55 | 0.51 | 113.56 | 1.296 | 270 | 11.1462
|  | Oct | 0.55 | 0.51 | 104.1 | 1.296 | 279 | 10.5583
|  | Nov | 0.55 | 0.51 | 94.63 | 1.296 | 270 | 9.2882
|  | Tlrad-CHN | [5 empty] | 82.1423
Inflitration Load for Different Setpoint Temperatures for Chennai
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 18 | 20.4 | 618.404 | 0.277 | 171.2979 | 270 | 46.2504
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 18 | 19 | 575.9645 | 0.277 | 159.5422 | 279 | 44.5123
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 18 | 17.9 | 542.6192 | 0.277 | 150.3055 | 279 | 41.9352
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 18 | 17 | 515.3366 | 0.277 | 142.7482 | 270 | 38.542
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 18 | 16 | 485.0227 | 0.277 | 134.3513 | 279 | 37.484
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 18 | 13.2 | 400.1437 | 0.277 | 110.8398 | 270 | 29.9268
|  | Tinf for setpoint 18 degrees C | [11 empty] | 238.6507
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 19 | 19.4 | 588.09 | 0.277 | 162.9009 | 270 | 43.9833
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 19 | 18 | 545.6506 | 0.277 | 151.1452 | 279 | 42.1695
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 19 | 16.9 | 512.3052 | 0.277 | 141.9086 | 279 | 39.5925
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 19 | 16 | 485.0227 | 0.277 | 134.3513 | 270 | 36.2748
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 19 | 15 | 454.7088 | 0.277 | 125.9543 | 279 | 35.1413
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 19 | 12.2 | 369.8298 | 0.277 | 102.4429 | 270 | 27.6596
|  | Tinf for setpoint 19 degrees C | [11 empty] | 224.8209
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 20 | 18.4 | 557.7761 | 0.277 | 154.504 | 270 | 41.7161
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 20 | 17 | 515.3366 | 0.277 | 142.7482 | 279 | 39.8268
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 20 | 15.9 | 481.9913 | 0.277 | 133.5116 | 279 | 37.2497
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 20 | 15 | 454.7088 | 0.277 | 125.9543 | 270 | 34.0077
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 20 | 14 | 424.3949 | 0.277 | 117.5574 | 279 | 32.7985
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 20 | 11.2 | 339.5159 | 0.277 | 94.0459 | 270 | 25.3924
|  | Tinf for setpoint 20 degrees C | [11 empty] | 210.9911
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 21 | 17.4 | 527.4622 | 0.277 | 146.107 | 270 | 39.4489
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 21 | 16 | 485.0227 | 0.277 | 134.3513 | 279 | 37.484
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 21 | 14.9 | 451.6774 | 0.277 | 125.1146 | 279 | 34.907
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 21 | 14 | 424.3949 | 0.277 | 117.5574 | 270 | 31.7405
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 21 | 13 | 394.081 | 0.277 | 109.1604 | 279 | 30.4558
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 21 | 10.2 | 309.202 | 0.277 | 85.6489 | 270 | 23.1252
|  | Tinf for setpoint 21 degrees C | [11 empty] | 197.1614
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 22 | 16.4 | 497.1483 | 0.277 | 137.7101 | 270 | 37.1817
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 22 | 15 | 454.7088 | 0.277 | 125.9543 | 279 | 35.1413
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 22 | 13.9 | 421.3635 | 0.277 | 116.7177 | 279 | 32.5642
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 22 | 13 | 394.081 | 0.277 | 109.1604 | 270 | 29.4733
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 22 | 12 | 363.767 | 0.277 | 100.7635 | 279 | 28.113
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 22 | 9.2 | 278.8881 | 0.277 | 77.252 | 270 | 20.858
|  | Tinf for setpoint 22 degrees C | [11 empty] | 183.3316
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 23 | 15.4 | 466.8344 | 0.277 | 129.3131 | 270 | 34.9145
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 23 | 14 | 424.3949 | 0.277 | 117.5574 | 279 | 32.7985
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 23 | 12.9 | 391.0496 | 0.277 | 108.3207 | 279 | 30.2215
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 23 | 12 | 363.767 | 0.277 | 100.7635 | 270 | 27.2061
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 23 | 11 | 333.4531 | 0.277 | 92.3665 | 279 | 25.7703
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 23 | 8.2 | 248.5741 | 0.277 | 68.855 | 270 | 18.5909
|  | Tinf for setpoint 23 degrees C | [11 empty] | 169.5018
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 24 | 14.4 | 436.5204 | 0.277 | 120.9162 | 270 | 32.6474
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 24 | 13 | 394.081 | 0.277 | 109.1604 | 279 | 30.4558
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 24 | 11.9 | 360.7356 | 0.277 | 99.9238 | 279 | 27.8787
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 24 | 11 | 333.4531 | 0.277 | 92.3665 | 270 | 24.939
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 24 | 10 | 303.1392 | 0.277 | 83.9696 | 279 | 23.4275
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 24 | 7.2 | 218.2602 | 0.277 | 60.4581 | 270 | 16.3237
|  | Tinf for setpoint 24 degrees C | [11 empty] | 155.672
Total Internal Load by People
|  | Month | People | SenL/person | CLF | SensL (W) | Latent/Person | LatentL (W) | Total peo L (W) | AC opn hrs |  | Total PL (KWh)
|  | Jun | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 270 |  | 113.4
|  | Jul | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 279 |  | 117.18
|  | Aug | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 279 |  | 117.18
|  | Sep | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 270 |  | 113.4
|  | Oct | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 279 |  | 117.18
|  | Nov | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 270 |  | 113.4
|  | Total Internal Load by People | [9 empty] | 691.74
Total Internal Heat Load of Lights per Year
|  | No. Bulbs | Watt Rating | bf | Fu | CLF | hrs (6hrs/day) | Tihlig(KWh)
|  | 3 | 60 | 1.24 | 0.66 | 0.8 | 1098 | 129.3989
|  | Total Internal Heat Load of Lights per Year | [5 empty] | 129.3989
Total Internal Heat Load-Equipment
|  | TV Rating W | Hrs /day | Total hrs | Tihe (KWh)
|  | 36 | 5 | 915 | 32.94
|  | Total load Equipment |  |  | 32.94
Summary of All Other Loads for Chennai
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 18 | 63.1083 | 82.1423 | 238.6507 | 691.74 | 129.3989 | 32.94 | 1237.9803
|  | 19 | 58.0922 | 82.1423 | 224.8209 | 691.74 | 129.3989 | 32.94 | 1219.1344
|  | 20 | 53.0761 | 82.1423 | 210.9911 | 691.74 | 129.3989 | 32.94 | 1200.2885
|  | 21 | 48.06 | 82.1423 | 197.1614 | 691.74 | 129.3989 | 32.94 | 1181.4426
|  | 22 | 43.0439 | 82.1423 | 183.3316 | 691.74 | 129.3989 | 32.94 | 1162.5967
|  | 23 | 38.4212 | 82.1423 | 169.5018 | 691.74 | 129.3989 | 32.94 | 1144.1441
|  | 24 | 33.3502 | 82.1423 | 155.672 | 691.74 | 129.3989 | 32.94 | 1125.2434
Thermal Conductive Load (TLgw-x) Calculated for Ahmedabad (Hot and Dry) for Setpoint TSP = 22°C
|  | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 18 | 7.5 | 7.6 | 18.1 | 2.35 | 1.296 | 270 | 14.8838
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 18 | 7.5 | 4.4 | 14.9 | 2.35 | 1.296 | 279 | 12.6609
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 18 | 7.5 | 1.8 | 12.3 | 2.35 | 1.296 | 279 | 10.4516
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 18 | 7.5 | 2.9 | 13.4 | 2.35 | 1.296 | 270 | 11.019
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 18 | 7.5 | 2 | 12.5 | 2.35 | 1.296 | 279 | 10.6215
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 18 | 7.5 | -1.95 | 8.55 | 2.35 | 1.296 | 270 | 7.0308
|  | TLgw-AMD (KWh)-18 Deg | [12 empty] | 66.6676
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 19 | 6.5 | 7.6 | 17.1 | 2.35 | 1.296 | 270 | 14.0615
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 19 | 6.5 | 4.4 | 13.9 | 2.35 | 1.296 | 279 | 11.8111
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 19 | 6.5 | 1.8 | 11.3 | 2.35 | 1.296 | 279 | 9.6019
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 19 | 6.5 | 2.9 | 12.4 | 2.35 | 1.296 | 270 | 10.1967
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 19 | 6.5 | 2 | 11.5 | 2.35 | 1.296 | 279 | 9.7718
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 19 | 6.5 | -1.95 | 7.55 | 2.35 | 1.296 | 270 | 6.2085
|  | TLgw-AMD (KWh)-19 Deg | [12 empty] | 61.6515
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 20 | 5.5 | 7.6 | 16.1 | 2.35 | 1.296 | 270 | 13.2392
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 20 | 5.5 | 4.4 | 12.9 | 2.35 | 1.296 | 279 | 10.9614
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 20 | 5.5 | 1.8 | 10.3 | 2.35 | 1.296 | 279 | 8.7521
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 20 | 5.5 | 2.9 | 11.4 | 2.35 | 1.296 | 270 | 9.3744
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 20 | 5.5 | 2 | 10.5 | 2.35 | 1.296 | 279 | 8.9221
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 20 | 5.5 | -1.95 | 6.55 | 2.35 | 1.296 | 270 | 5.3861
|  | TLgw-AMD (KWh)-20 Deg | [12 empty] | 56.6354
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 21 | 4.5 | 7.6 | 15.1 | 2.35 | 1.296 | 270 | 12.4169
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 21 | 4.5 | 4.4 | 11.9 | 2.35 | 1.296 | 279 | 10.1117
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 21 | 4.5 | 1.8 | 9.3 | 2.35 | 1.296 | 279 | 7.9024
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 21 | 4.5 | 2.9 | 10.4 | 2.35 | 1.296 | 270 | 8.552
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 21 | 4.5 | 2 | 9.5 | 2.35 | 1.296 | 279 | 8.0724
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 21 | 4.5 | -1.95 | 5.55 | 2.35 | 1.296 | 270 | 4.5638
|  | TLgw-AMD (KWh)-21 Deg | [12 empty] | 51.6193
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 22 | 3.5 | 7.6 | 14.1 | 2.35 | 1.296 | 270 | 11.5946
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 22 | 3.5 | 4.4 | 10.9 | 2.35 | 1.296 | 279 | 9.262
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 22 | 3.5 | 1.8 | 8.3 | 2.35 | 1.296 | 279 | 7.0527
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 22 | 3.5 | 2.9 | 9.4 | 2.35 | 1.296 | 270 | 7.7297
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 22 | 3.5 | 2 | 8.5 | 2.35 | 1.296 | 279 | 7.2226
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 22 | 3.5 | -1.95 | 4.55 | 2.35 | 1.296 | 270 | 3.7415
|  | TLgw-AMD (KWh)-22 Deg | [12 empty] | 46.6032
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 23 | 2.5 | 7.6 | 13.1 | 2.35 | 1.296 | 270 | 10.7723
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 23 | 2.5 | 4.4 | 9.9 | 2.35 | 1.296 | 279 | 8.4123
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 23 | 2.5 | 1.8 | 7.3 | 2.35 | 1.296 | 279 | 6.203
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 23 | 2.5 | 2.9 | 8.4 | 2.35 | 1.296 | 270 | 6.9074
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 23 | 2.5 | 2 | 7.5 | 2.35 | 1.296 | 279 | 6.3729
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 23 | 2.5 | -1.95 | 3.55 | 2.35 | 1.296 | 270 | 2.9192
|  | TLgw-AMD (KWh)-23 Deg | [12 empty] | 41.5871
|  | Jun | 41.9 | 9.8 | 4.9 | 37 | 3 | 24 | 1.5 | 7.6 | 12.1 | 2.35 | 1.296 | 270 | 9.95
|  | Jul | 36.9 | 6.2 | 3.1 | 33.8 | 3 | 24 | 1.5 | 4.4 | 8.9 | 2.35 | 1.296 | 279 | 7.5625
|  | Aug | 34.1 | 5.8 | 2.9 | 31.2 | 3 | 24 | 1.5 | 1.8 | 6.3 | 2.35 | 1.296 | 279 | 5.3533
|  | Sep | 36.1 | 7.6 | 3.8 | 32.3 | 3 | 24 | 1.5 | 2.9 | 7.4 | 2.35 | 1.296 | 270 | 6.0851
|  | Oct | 37.8 | 12.8 | 6.4 | 31.4 | 3 | 24 | 1.5 | 2 | 6.5 | 2.35 | 1.296 | 279 | 5.5232
|  | Nov | 34.8 | 14.7 | 7.35 | 27.45 | 3 | 24 | 1.5 | -1.95 | 2.55 | 2.35 | 1.296 | 270 | 2.0969
|  | TLgw-AMD (KWh)-24 Deg | [12 empty] | 36.571
Annual Radiation Thermal Load Through Glass Window- Ahmedabad
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jun | 0.55 | 0.51 | 173.5 | 1.296 | 270 | 17.0295
|  | Jul | 0.55 | 0.51 | 141.95 | 1.296 | 279 | 14.3972
|  | Aug | 0.55 | 0.51 | 119.87 | 1.296 | 279 | 12.1577
|  | Sep | 0.55 | 0.51 | 110.41 | 1.296 | 270 | 10.837
|  | Oct | 0.55 | 0.51 | 97.79 | 1.296 | 279 | 9.9183
|  | Nov | 0.55 | 0.51 | 85.17 | 1.296 | 270 | 8.3597
|  | Tlrad-AMD | [5 empty] | 72.6993
Inflitration Load for Different Setpoint Temperatures for Ahmedabad
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 18 | 23.9 | 724.5027 | 0.277 | 200.6872 | 270 | 54.1856
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 18 | 18.9 | 572.9331 | 0.277 | 158.7025 | 279 | 44.278
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 18 | 16.1 | 488.0541 | 0.277 | 135.191 | 279 | 37.7183
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 18 | 18.1 | 548.6819 | 0.277 | 151.9849 | 270 | 41.0359
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 18 | 19.8 | 600.2156 | 0.277 | 166.2597 | 279 | 46.3865
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 18 | 16.8 | 509.2738 | 0.277 | 141.0689 | 270 | 38.0886
|  | Tinf for setpoint 18 degrees C | [11 empty] | 261.6928
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 19 | 22.9 | 694.1888 | 0.277 | 192.2903 | 270 | 51.9184
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 19 | 17.9 | 542.6192 | 0.277 | 150.3055 | 279 | 41.9352
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 19 | 15.1 | 457.7402 | 0.277 | 126.794 | 279 | 35.3755
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 19 | 17.1 | 518.368 | 0.277 | 143.5879 | 270 | 38.7687
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 19 | 18.8 | 569.9017 | 0.277 | 157.8628 | 279 | 44.0437
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 19 | 15.8 | 478.9599 | 0.277 | 132.6719 | 270 | 35.8214
|  | Tinf for setpoint 19 degrees C | [11 empty] | 247.863
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 20 | 21.9 | 663.8748 | 0.277 | 183.8933 | 270 | 49.6512
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 20 | 16.9 | 512.3052 | 0.277 | 141.9086 | 279 | 39.5925
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 20 | 14.1 | 427.4263 | 0.277 | 118.3971 | 279 | 33.0328
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 20 | 16.1 | 488.0541 | 0.277 | 135.191 | 270 | 36.5016
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 20 | 17.8 | 539.5878 | 0.277 | 149.4658 | 279 | 41.701
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 20 | 14.8 | 448.646 | 0.277 | 124.2749 | 270 | 33.5542
|  | Tinf for setpoint 20 degrees C | [11 empty] | 234.0332
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 21 | 20.9 | 633.5609 | 0.277 | 175.4964 | 270 | 47.384
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 21 | 15.9 | 481.9913 | 0.277 | 133.5116 | 279 | 37.2497
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 21 | 13.1 | 397.1123 | 0.277 | 110.0001 | 279 | 30.69
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 21 | 15.1 | 457.7402 | 0.277 | 126.794 | 270 | 34.2344
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 21 | 16.8 | 509.2738 | 0.277 | 141.0689 | 279 | 39.3582
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 21 | 13.8 | 418.3321 | 0.277 | 115.878 | 270 | 31.2871
|  | Tinf for setpoint 21 degrees C | [11 empty] | 220.2034
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 22 | 19.9 | 603.247 | 0.277 | 167.0994 | 270 | 45.1168
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 22 | 14.9 | 451.6774 | 0.277 | 125.1146 | 279 | 34.907
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 22 | 12.1 | 366.7984 | 0.277 | 101.6032 | 279 | 28.3473
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 22 | 14.1 | 427.4263 | 0.277 | 118.3971 | 270 | 31.9672
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 22 | 15.8 | 478.9599 | 0.277 | 132.6719 | 279 | 37.0155
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 22 | 12.8 | 388.0182 | 0.277 | 107.481 | 270 | 29.0199
|  | Tinf for setpoint 22 degrees C | [11 empty] | 206.3737
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 23 | 18.9 | 572.9331 | 0.277 | 158.7025 | 270 | 42.8497
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 23 | 13.9 | 421.3635 | 0.277 | 116.7177 | 279 | 32.5642
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 23 | 11.1 | 336.4845 | 0.277 | 93.2062 | 279 | 26.0045
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 23 | 13.1 | 397.1123 | 0.277 | 110.0001 | 270 | 29.7
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 23 | 14.8 | 448.646 | 0.277 | 124.2749 | 279 | 34.6727
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 23 | 11.8 | 357.7043 | 0.277 | 99.0841 | 270 | 26.7527
|  | Tinf for setpoint 23 degrees C | [11 empty] | 192.5439
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 41.9 | 24 | 17.9 | 542.6192 | 0.277 | 150.3055 | 270 | 40.5825
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 24 | 12.9 | 391.0496 | 0.277 | 108.3207 | 279 | 30.2215
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 24 | 10.1 | 306.1706 | 0.277 | 84.8093 | 279 | 23.6618
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 24 | 12.1 | 366.7984 | 0.277 | 101.6032 | 270 | 27.4329
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 24 | 13.8 | 418.3321 | 0.277 | 115.878 | 279 | 32.33
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 34.8 | 24 | 10.8 | 327.3903 | 0.277 | 90.6871 | 270 | 24.4855
|  | Tinf for setpoint 24 degrees C | [11 empty] | 178.7141
Summary of All Other Loads for Ahmedabad
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 18 | 66.6676 | 72.6993 | 261.6928 | 691.74 | 129.3989 | 32.94 | 1255.1386
|  | 19 | 61.6515 | 72.6993 | 247.863 | 691.74 | 129.3989 | 32.94 | 1236.2927
|  | 20 | 56.6354 | 72.6993 | 234.0332 | 691.74 | 129.3989 | 32.94 | 1217.4468
|  | 21 | 51.6193 | 72.6993 | 220.2034 | 691.74 | 129.3989 | 32.94 | 1198.6009
|  | 22 | 46.6032 | 72.6993 | 206.3737 | 691.74 | 129.3989 | 32.94 | 1179.755
|  | 23 | 41.5871 | 72.6993 | 192.5439 | 691.74 | 129.3989 | 32.94 | 1160.9091
|  | 24 | 36.571 | 72.6993 | 178.7141 | 691.74 | 129.3989 | 32.94 | 1142.0632
Thermal Conductive Load (TLgw-x) Calculated for Delhi (Composite) for Setpoint TSP = 22°C
|  | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 18 | 7.5 | 9.35 | 19.85 | 2.35 | 1.296 | 270 | 16.3229
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 18 | 7.5 | 6.05 | 16.55 | 2.35 | 1.296 | 279 | 14.0629
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 18 | 7.5 | 4.1 | 14.6 | 2.35 | 1.296 | 279 | 12.4059
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 18 | 7.5 | 3.25 | 13.75 | 2.35 | 1.296 | 270 | 11.3068
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 18 | 7.5 | -0.1 | 10.4 | 2.35 | 1.296 | 279 | 8.8371
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 18 | 7.5 | -5.1 | 5.4 | 2.35 | 1.296 | 270 | 4.4405
|  | TLgw-DEL (KWh)-18 Deg | [12 empty] | 67.3761
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 19 | 6.5 | 9.35 | 18.85 | 2.35 | 1.296 | 270 | 15.5006
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 19 | 6.5 | 6.05 | 15.55 | 2.35 | 1.296 | 279 | 13.2132
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 19 | 6.5 | 4.1 | 13.6 | 2.35 | 1.296 | 279 | 11.5562
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 19 | 6.5 | 3.25 | 12.75 | 2.35 | 1.296 | 270 | 10.4845
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 19 | 6.5 | -0.1 | 9.4 | 2.35 | 1.296 | 279 | 7.9874
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 19 | 6.5 | -5.1 | 4.4 | 2.35 | 1.296 | 270 | 3.6182
|  | TLgw-DEL (KWh)-19 Deg | [12 empty] | 62.36
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 20 | 5.5 | 9.35 | 17.85 | 2.35 | 1.296 | 270 | 14.6783
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 20 | 5.5 | 6.05 | 14.55 | 2.35 | 1.296 | 279 | 12.3635
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 20 | 5.5 | 4.1 | 12.6 | 2.35 | 1.296 | 279 | 10.7065
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 20 | 5.5 | 3.25 | 11.75 | 2.35 | 1.296 | 270 | 9.6622
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 20 | 5.5 | -0.1 | 8.4 | 2.35 | 1.296 | 279 | 7.1377
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 20 | 5.5 | -5.1 | 3.4 | 2.35 | 1.296 | 270 | 2.7959
|  | TLgw-DEL (KWh)-20 Deg | [12 empty] | 57.3439
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 21 | 4.5 | 9.35 | 16.85 | 2.35 | 1.296 | 270 | 13.856
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 21 | 4.5 | 6.05 | 13.55 | 2.35 | 1.296 | 279 | 11.5137
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 21 | 4.5 | 4.1 | 11.6 | 2.35 | 1.296 | 279 | 9.8568
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 21 | 4.5 | 3.25 | 10.75 | 2.35 | 1.296 | 270 | 8.8399
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 21 | 4.5 | -0.1 | 7.4 | 2.35 | 1.296 | 279 | 6.2879
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 21 | 4.5 | -5.1 | 2.4 | 2.35 | 1.296 | 270 | 1.9735
|  | TLgw-DEL (KWh)-21 Deg | [12 empty] | 52.3278
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 22 | 3.5 | 9.35 | 15.85 | 2.35 | 1.296 | 270 | 13.0336
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 22 | 3.5 | 6.05 | 12.55 | 2.35 | 1.296 | 279 | 10.664
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 22 | 3.5 | 4.1 | 10.6 | 2.35 | 1.296 | 279 | 9.0071
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 22 | 3.5 | 3.25 | 9.75 | 2.35 | 1.296 | 270 | 8.0175
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 22 | 3.5 | -0.1 | 6.4 | 2.35 | 1.296 | 279 | 5.4382
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 22 | 3.5 | -5.1 | 1.4 | 2.35 | 1.296 | 270 | 1.1512
|  | TLgw-DEL (KWh)-22 Deg | [12 empty] | 47.3117
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 23 | 2.5 | 9.35 | 14.85 | 2.35 | 1.296 | 270 | 12.2113
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 23 | 2.5 | 6.05 | 11.55 | 2.35 | 1.296 | 279 | 9.8143
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 23 | 2.5 | 4.1 | 9.6 | 2.35 | 1.296 | 279 | 8.1573
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 23 | 2.5 | 3.25 | 8.75 | 2.35 | 1.296 | 270 | 7.1952
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 23 | 2.5 | -0.1 | 5.4 | 2.35 | 1.296 | 279 | 4.5885
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 23 | 2.5 | -5.1 | 0.4 | 2.35 | 1.296 | 270 | 0.32892
|  | TLgw-DEL (KWh)-23 Deg | [12 empty] | 42.2956
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 24 | 1.5 | 9.35 | 13.85 | 2.35 | 1.296 | 270 | 11.389
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 24 | 1.5 | 6.05 | 10.55 | 2.35 | 1.296 | 279 | 8.9646
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 24 | 1.5 | 4.1 | 8.6 | 2.35 | 1.296 | 279 | 7.3076
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 24 | 1.5 | 3.25 | 7.75 | 2.35 | 1.296 | 270 | 6.3729
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 24 | 1.5 | -0.1 | 4.4 | 2.35 | 1.296 | 279 | 3.7388
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 24 | 1.5 | -5.1 | -0.6 | 2.35 | 1.296 | 270 | -0.49339
|  | TLgw-DEL (KWh)-24 Deg | [12 empty] | 37.2795
|  | Jun | 43.8 | 10.1 | 5.05 | 38.75 | 3 | 25 | 0.5 | 9.35 | 12.85 | 2.35 | 1.296 | 270 | 10.5667
|  | Jul | 39 | 7.1 | 3.55 | 35.45 | 3 | 25 | 0.5 | 6.05 | 9.55 | 2.35 | 1.296 | 279 | 8.1148
|  | Aug | 36.9 | 6.8 | 3.4 | 33.5 | 3 | 25 | 0.5 | 4.1 | 7.6 | 2.35 | 1.296 | 279 | 6.4579
|  | Sep | 36.8 | 8.3 | 4.15 | 32.65 | 3 | 25 | 0.5 | 3.25 | 6.75 | 2.35 | 1.296 | 270 | 5.5506
|  | Oct | 35.2 | 11.8 | 5.9 | 29.3 | 3 | 25 | 0.5 | -0.1 | 3.4 | 2.35 | 1.296 | 279 | 2.8891
|  | Nov | 30.8 | 13 | 6.5 | 24.3 | 3 | 25 | 0.5 | -5.1 | -1.6 | 2.35 | 1.296 | 270 | -1.3157
|  | TLgw-DEL (KWh)-24 Deg | [12 empty] | 32.2634
Annual Radiation Thermal Load Through Glass Window- Delhi
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jun | 0.55 | 0.51 | 138.8 | 1.296 | 270 | 13.6236
|  | Jul | 0.55 | 0.51 | 126.18 | 1.296 | 279 | 12.7977
|  | Aug | 0.55 | 0.51 | 116.71 | 1.296 | 279 | 11.8372
|  | Sep | 0.55 | 0.51 | 104.1 | 1.296 | 270 | 10.2177
|  | Oct | 0.55 | 0.51 | 88.32 | 1.296 | 279 | 8.9578
|  | Nov | 0.55 | 0.51 | 75.71 | 1.296 | 270 | 7.4311
|  | Tlrad-AMD | [5 empty] | 64.8651
Inflitration Load for Different Setpoint Temperatures for Delhi
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 18 | 25.8 | 782.0991 | 0.277 | 216.6415 | 270 | 58.4932
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 18 | 21 | 636.5923 | 0.277 | 176.3361 | 279 | 49.1978
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 18 | 18.9 | 572.9331 | 0.277 | 158.7025 | 279 | 44.278
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 18 | 18.8 | 569.9017 | 0.277 | 157.8628 | 270 | 42.6229
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 18 | 17.2 | 521.3994 | 0.277 | 144.4276 | 279 | 40.2953
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 18 | 12.8 | 388.0182 | 0.277 | 107.481 | 270 | 29.0199
|  | Tinf for setpoint 18 degrees C | [11 empty] | 176.394
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 19 | 24.8 | 751.7852 | 0.277 | 208.2445 | 270 | 56.226
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 19 | 20 | 606.2784 | 0.277 | 167.9391 | 279 | 46.855
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 19 | 17.9 | 542.6192 | 0.277 | 150.3055 | 279 | 41.9352
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 19 | 17.8 | 539.5878 | 0.277 | 149.4658 | 270 | 40.3558
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 19 | 16.2 | 491.0855 | 0.277 | 136.0307 | 279 | 37.9526
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 19 | 11.8 | 357.7043 | 0.277 | 99.0841 | 270 | 26.7527
|  | Tinf for setpoint 19 degrees C | [11 empty] | 167.0986
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 20 | 23.8 | 721.4713 | 0.277 | 199.8475 | 270 | 53.9588
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 20 | 19 | 575.9645 | 0.277 | 159.5422 | 279 | 44.5123
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 20 | 16.9 | 512.3052 | 0.277 | 141.9086 | 279 | 39.5925
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 20 | 16.8 | 509.2738 | 0.277 | 141.0689 | 270 | 38.0886
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 20 | 15.2 | 460.7716 | 0.277 | 127.6337 | 279 | 35.6098
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 20 | 10.8 | 327.3903 | 0.277 | 90.6871 | 270 | 24.4855
|  | Tinf for setpoint 20 degrees C | [11 empty] | 157.8031
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 21 | 22.8 | 691.1574 | 0.277 | 191.4506 | 270 | 51.6917
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 21 | 18 | 545.6506 | 0.277 | 151.1452 | 279 | 42.1695
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 21 | 15.9 | 481.9913 | 0.277 | 133.5116 | 279 | 37.2497
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 21 | 15.8 | 478.9599 | 0.277 | 132.6719 | 270 | 35.8214
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 21 | 14.2 | 430.4577 | 0.277 | 119.2368 | 279 | 33.2671
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 21 | 9.8 | 297.0764 | 0.277 | 82.2902 | 270 | 22.2183
|  | Tinf for setpoint 21 degrees C | [11 empty] | 148.5077
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 22 | 21.8 | 660.8434 | 0.277 | 183.0536 | 270 | 49.4245
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 22 | 17 | 515.3366 | 0.277 | 142.7482 | 279 | 39.8268
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 22 | 14.9 | 451.6774 | 0.277 | 125.1146 | 279 | 34.907
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 22 | 14.8 | 448.646 | 0.277 | 124.2749 | 270 | 33.5542
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 22 | 13.2 | 400.1437 | 0.277 | 110.8398 | 279 | 30.9243
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 22 | 8.8 | 266.7625 | 0.277 | 73.8932 | 270 | 19.9512
|  | Tinf for setpoint 22 degrees C | [11 empty] | 139.2123
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 22 | 21.8 | 660.8434 | 0.277 | 183.0536 | 270 | 49.4245
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 23 | 16 | 485.0227 | 0.277 | 134.3513 | 279 | 37.484
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 23 | 13.9 | 421.3635 | 0.277 | 116.7177 | 279 | 32.5642
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 23 | 13.8 | 418.3321 | 0.277 | 115.878 | 270 | 31.2871
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 23 | 12.2 | 369.8298 | 0.277 | 102.4429 | 279 | 28.5816
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 22 | 8.8 | 266.7625 | 0.277 | 73.8932 | 270 | 19.9512
|  | Tinf for setpoint 23 degrees C | [11 empty] | 129.9169
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 43.8 | 22 | 21.8 | 660.8434 | 0.277 | 183.0536 | 270 | 49.4245
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 39 | 24 | 15 | 454.7088 | 0.277 | 125.9543 | 279 | 35.1413
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 36.9 | 24 | 12.9 | 391.0496 | 0.277 | 108.3207 | 279 | 30.2215
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 24 | 12.8 | 388.0182 | 0.277 | 107.481 | 270 | 29.0199
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 24 | 11.2 | 339.5159 | 0.277 | 94.0459 | 279 | 26.2388
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 22 | 8.8 | 266.7625 | 0.277 | 73.8932 | 270 | 19.9512
|  | Tinf for setpoint 24 degrees C | [11 empty] | 120.6214
Summary of All Other Loads for Delhi
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 18 | 67.3761 | 64.8651 | 176.394 | 691.74 | 129.3989 | 32.94 | 1162.7141
|  | 19 | 62.36 | 64.8651 | 167.0986 | 691.74 | 129.3989 | 32.94 | 1148.4026
|  | 20 | 57.3439 | 64.8651 | 157.8031 | 691.74 | 129.3989 | 32.94 | 1134.0911
|  | 21 | 52.3278 | 64.8651 | 148.5077 | 691.74 | 129.3989 | 32.94 | 1119.7795
|  | 22 | 47.3117 | 64.8651 | 139.2123 | 691.74 | 129.3989 | 32.94 | 1105.468
|  | 23 | 42.2956 | 64.8651 | 129.9169 | 691.74 | 129.3989 | 32.94 | 1091.1565
|  | 24 | 37.2795 | 64.8651 | 120.6214 | 691.74 | 129.3989 | 32.94 | 1076.8449

## All Season Dengue Endemic_IN
|  | Balance Point Temperature, Annual Variable Degree Days, Thermal Load of Living Space and Annual Electricity Consumption Calculations for Chennai- Baseline and Solar Electricity Scenarios | [30 empty] | LDRZ Setpoint Adjsuted Preference %
|  | Month | [8 empty] | VCDDmth | AC hrs/24 hrs (fAC) | Conv (24/1000) KWh |  |  | Annual VCDD |  |  |  | Annual VCDD |  |  |  | Annual VCDD |  | All Other Heat Loads | BE+Other Loads | 10%SF |  | EER | Elec. Cons. |  | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Jan | 22 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9605 | 216.7 | [21 empty] | 22 | 16 | 0.34783
|  | Feb | 22 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9434 | 233.5 | [21 empty] | 23 | 10 | 0.21739
|  | Mar | 22 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9319 | 326.1 | [21 empty] | 24 | 20 | 0.43478
|  | Apr | 22 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.909 | 364.1 | [22 empty] | 46 | 1
|  | May | 22 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8347 | 419.6
|  | Jun | 22 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.7545 | 360.7
|  | July | 22 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8175 | 362.9
|  | Aug | 22 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8976 | 354
|  | Sep | 22 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9262 | 348.1
|  | Oct | 22 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9434 | 322.7
|  | Nov | 22 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9605 | 252.8
|  | Dec | 22 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9662 | 240.3
|  | Annual VCDD | [8 empty] | 3801.5 | 0.66667 | 0.024 | 3.59 | 12.96 | 3801.5 | 2829.9218 | 3.94 | 12.96 | 3801.5 | 3105.8194 | 2.13 | 41.904 | 3801.5 | 5428.8777 | 3849.2555 | 15213.8744 | 1521.3874 | 16735.2619 | 3.1 | 5398 | 22
|  | Month | [8 empty] | VCDDmth
|  | Jan | 23 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9605 | 185.7
|  | Feb | 23 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9434 | 205.5
|  | Mar | 23 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9319 | 295.1
|  | Apr | 23 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.909 | 334.1
|  | May | 23 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8347 | 388.6
|  | Jun | 23 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.7545 | 330.7
|  | July | 23 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8175 | 331.9
|  | Aug | 23 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8976 | 323
|  | Sep | 23 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9262 | 318.1
|  | Oct | 23 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9434 | 291.7
|  | Nov | 23 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9605 | 222.8
|  | Dec | 23 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9662 | 209.3
|  | Annual VCDD | [8 empty] | 3436.5 | 0.66667 | 0.024 | 3.59 | 12.96 | 3436.5 | 2558.2076 | 3.94 | 12.96 | 3436.5 | 2807.615 | 2.13 | 41.904 | 3436.5 | 4907.6255 | 3771.8349 | 14045.283 | 1404.5283 | 15449.8113 | 3.1 | 4984 | 23
|  | Month | [8 empty] | VCDDmth
|  | Jan | 24 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9605 | 154.7
|  | Feb | 24 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9434 | 177.5
|  | Mar | 24 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9319 | 264.1
|  | Apr | 24 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.909 | 304.1
|  | May | 24 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8347 | 357.6
|  | Jun | 24 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.7545 | 300.7
|  | Jul | 24 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8175 | 300.9
|  | Aug | 24 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8976 | 292
|  | Sep | 24 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9262 | 288.1
|  | Oct | 24 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9434 | 260.7
|  | Nov | 24 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9605 | 192.8
|  | Dec | 24 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9662 | 178.3
|  | Annual VCDD | [8 empty] | 3071.5 | 0.66667 | 0.024 | 3.59 | 12.96 | 3071.5 | 2286.4934 | 3.94 | 12.96 | 3071.5 | 2509.4106 | 2.13 | 41.904 | 3071.5 | 4386.3733 | 3694.4143 | 12876.6915 | 1287.6692 | 14164.3607 | 3.1 | 4569 | 24
|  | Avg Annual VCDD Based on Consumer Setpoint Prefreneces for Chennai-India (Warm and Humid) for Low Dengue Risk Zone (LDRZ) | [28 empty] | 4947.5652
|  | Month | [8 empty] | VCDDmth
|  | Jan | 25 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9605 | 123.7
|  | Feb | 25 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9434 | 149.5
|  | Mar | 25 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9319 | 233.1
|  | Apr | 25 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.909 | 274.1 | [21 empty] | MDRZ Setpoint Adjsuted Preference %
|  | May | 25 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8347 | 326.6 | [21 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Jun | 25 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.7545 | 270.7 | [21 empty] | 25 | 12 | 1
|  | Jul | 25 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8175 | 269.9
|  | Aug | 25 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8976 | 261
|  | Sep | 25 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9262 | 258.1
|  | Oct | 25 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9434 | 229.7
|  | Nov | 25 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9605 | 162.8
|  | Dec | 25 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9662 | 147.3
|  | Annual VCDD | [8 empty] | 2706.5 | 0.66667 | 0.024 | 3.59 | 12.96 | 2706.5 | 2014.7792 | 3.94 | 12.96 | 2706.5 | 2211.2062 | 2.13 | 41.904 | 2706.5 | 3865.121 | 3616.9936 | 11708.1001 | 1170.81 | 12878.9101 | 3.1 | 4154
|  | Avg Annual VCDD Based on Consumer Setpoint Prefreneces for Chennai-India (Warm and Humid) for Moderate Dengue Risk Zone (MDRZ) | [28 empty] | 4154 | 25
|  | Month | [8 empty] | VCDDmth
|  | Jan | 26 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9605 | 93
|  | Feb | 26 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9434 | 121.6
|  | Mar | 26 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9319 | 202.1
|  | Apr | 26 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.909 | 244.1
|  | May | 26 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8347 | 295.6
|  | Jun | 26 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.7545 | 240.7
|  | July | 26 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8175 | 238.9
|  | Aug | 26 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8976 | 230
|  | Sep | 26 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9262 | 228.1
|  | Oct | 26 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9434 | 198.7
|  | Nov | 26 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9605 | 132.8
|  | Dec | 26 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9662 | 116.3
|  | Annual VCDD | [8 empty] | 2341.9 | 0.66667 | 0.024 | 3.59 | 12.96 | 2341.9 | 1743.3628 | 3.94 | 12.96 | 2341.9 | 1913.3286 | 2.13 | 41.904 | 2341.9 | 3344.44 | 3539.573 | 10540.7044 | 1054.0704 | 11594.7749 | 3.1 | 3740 | 26 | HDRZ Setpoint Adjsuted Preference %
|  | Month | [8 empty] | VCDDmth | [21 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Jan | 27 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9605 | 64.8 | [21 empty] | 26 | 10 | 0.5
|  | Feb | 27 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9434 | 94.8 | [21 empty] | 27 | 8 | 0.4
|  | Mar | 27 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9319 | 171.1 | [21 empty] | 28 | 2 | 0.1
|  | Apr | 27 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.909 | 214.1 | [22 empty] | 20
|  | May | 27 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8347 | 264.6
|  | Jun | 27 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.7545 | 210.7
|  | Jul | 27 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8175 | 207.9
|  | Aug | 27 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8976 | 199
|  | Sep | 27 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9262 | 198.1
|  | Oct | 27 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9434 | 167.7
|  | Nov | 27 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9605 | 103.5
|  | Dec | 27 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9662 | 85.6
|  | Annual VCDD | [8 empty] | 1981.9 | 0.66667 | 0.024 | 3.59 | 12.96 | 1981.9 | 1475.3708 | 3.94 | 12.96 | 1981.9 | 1619.2091 | 2.13 | 41.904 | 1981.9 | 2830.3282 | 3462.1524 | 9387.0605 | 938.7061 | 10325.7666 | 3.1 | 3331 | 27
|  | Month | [8 empty] | VCDDmth
|  | Jan | 28 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9605 | 42.6
|  | Feb | 28 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9434 | 71.5
|  | Mar | 28 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9319 | 140.5
|  | Apr | 28 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.909 | 184.1
|  | May | 28 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8347 | 233.6
|  | Jun | 28 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.7545 | 180.7
|  | Jul | 28 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8175 | 177
|  | Aug | 28 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8976 | 168
|  | Sep | 28 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9262 | 168.3
|  | Oct | 28 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9434 | 136.9
|  | Nov | 28 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9605 | 75.6
|  | Dec | 28 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9662 | 57.7
|  | Annual VCDD | [8 empty] | 1636.5 | 0.66667 | 0.024 | 3.59 | 12.96 | 1636.5 | 1218.2473 | 3.94 | 12.96 | 1636.5 | 1337.0179 | 2.13 | 41.904 | 1636.5 | 2337.0665 | 3384.7318 | 8277.0635 | 827.7063 | 9104.7698 | 3.1 | 2937 | 28
|  | Avg Annual VCDD Based on Consumer Setpoint Prefreneces for Chennai-India (Warm and Humid) for High Dengue Risk Zone (HDRZ) | [28 empty] | 3496
CLTDgw-avg (°C) for AC Opn hrs. |  | Thermal Conductive Load (TLgw-x) Calculated for Three Climate Zones
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 22°C
AC Opn hrs. | CLTDgw (°C) | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
00.00-01.00 | 1 | Jan | 30.2 | 7.9 | 3.95 | 26.25 | 1.75 | 22 | 3.5 | -3.15 | 2.1 | 3.75 | 1.296 | 496 | 5.0622
01.00-02.00 | 1 | Feb | 32.2 | 8.7 | 4.35 | 27.85 | 1.75 | 22 | 3.5 | -1.55 | 3.7 | 3.75 | 1.296 | 448 | 8.0559
02.00-03.00 | 0 | Mar | 34.9 | 8.9 | 4.45 | 30.45 | 1.75 | 22 | 3.5 | 1.05 | 6.3 | 3.75 | 1.296 | 496 | 15.1865
03.00-04.00 | -1 | Apr | 36.8 | 8.2 | 4.1 | 32.7 | 1.75 | 22 | 3.5 | 3.3 | 8.55 | 3.75 | 1.296 | 480 | 19.9454
04.00-05.00 | -1 | May | 39.8 | 9.2 | 4.6 | 35.2 | 1.75 | 22 | 3.5 | 5.8 | 11.05 | 3.75 | 1.296 | 496 | 26.6367
05.00-06.00 | -1 | Jun | 38.4 | 8.8 | 4.4 | 34 | 1.75 | 22 | 3.5 | 4.6 | 9.85 | 3.75 | 1.296 | 480 | 22.9781
06.00-07.00 | -1 | Jul | 37 | 8.1 | 4.05 | 32.95 | 1.75 | 22 | 3.5 | 3.55 | 8.8 | 3.75 | 1.296 | 496 | 21.2129
07.00-08.00 | -1 | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 1.75 | 22 | 3.5 | 2.55 | 7.8 | 3.75 | 1.296 | 496 | 18.8024
08.00-09.00 | 0 | Sep | 35 | 7.7 | 3.85 | 31.15 | 1.75 | 22 | 3.5 | 1.75 | 7 | 3.75 | 1.296 | 480 | 16.3296
17.00-18.00 | 7 | Oct | 34 | 6.7 | 3.35 | 30.65 | 1.75 | 22 | 3.5 | 1.25 | 6.5 | 3.75 | 1.296 | 496 | 15.6686
18.00-19.00 | 7 | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 1.75 | 22 | 3.5 | -1.25 | 4 | 3.75 | 1.296 | 480 | 9.3312
19.00-20.00 | 6 | Dec | 30.1 | 6.7 | 3.35 | 26.75 | 1.75 | 22 | 3.5 | -2.65 | 2.6 | 3.75 | 1.296 | 496 | 6.2675
20.00-21.00 | 4 | TLgw-CHN (KWh) | [12 empty] | 185.477
21.00-22.00 | 3 | Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 23°C
22.00-23.00 | 2 | Jan | 30.2 | 7.9 | 3.95 | 26.25 | 1.75 | 23 | 2.5 | -3.15 | 1.1 | 3.75 | 1.296 | 496 | 2.6516
23.00-00.00 | 2 | Feb | 32.2 | 8.7 | 4.35 | 27.85 | 1.75 | 23 | 2.5 | -1.55 | 2.7 | 3.75 | 1.296 | 448 | 5.8787
CLTDgw-avg (°C) | 1.75 | Mar | 34.9 | 8.9 | 4.45 | 30.45 | 1.75 | 23 | 2.5 | 1.05 | 5.3 | 3.75 | 1.296 | 496 | 12.776
|  | Apr | 36.8 | 8.2 | 4.1 | 32.7 | 1.75 | 23 | 2.5 | 3.3 | 7.55 | 3.75 | 1.296 | 480 | 17.6126
|  | May | 39.8 | 9.2 | 4.6 | 35.2 | 1.75 | 23 | 2.5 | 5.8 | 10.05 | 3.75 | 1.296 | 496 | 24.2261
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 1.75 | 23 | 2.5 | 4.6 | 8.85 | 3.75 | 1.296 | 480 | 20.6453
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 1.75 | 23 | 2.5 | 3.55 | 7.8 | 3.75 | 1.296 | 496 | 18.8024
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 1.75 | 23 | 2.5 | 2.55 | 6.8 | 3.75 | 1.296 | 496 | 16.3918
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 1.75 | 23 | 2.5 | 1.75 | 6 | 3.75 | 1.296 | 480 | 13.9968
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 1.75 | 23 | 2.5 | 1.25 | 5.5 | 3.75 | 1.296 | 496 | 13.2581
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 1.75 | 23 | 2.5 | -1.25 | 3 | 3.75 | 1.296 | 480 | 6.9984
|  | Dec | 30.1 | 6.7 | 3.35 | 26.75 | 1.75 | 23 | 2.5 | -2.65 | 1.6 | 3.75 | 1.296 | 496 | 3.8569
|  | TLgw-CHN (KWh) | [12 empty] | 157.0946
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 24°C
|  | Jan | 30.2 | 7.9 | 3.95 | 26.25 | 1.75 | 24 | 1.5 | -3.15 | 0.1 | 3.75 | 1.296 | 496 | 0.24106
|  | Feb | 32.2 | 8.7 | 4.35 | 27.85 | 1.75 | 24 | 1.5 | -1.55 | 1.7 | 3.75 | 1.296 | 448 | 3.7014
|  | Mar | 34.9 | 8.9 | 4.45 | 30.45 | 1.75 | 24 | 1.5 | 1.05 | 4.3 | 3.75 | 1.296 | 496 | 10.3654
|  | Apr | 36.8 | 8.2 | 4.1 | 32.7 | 1.75 | 24 | 1.5 | 3.3 | 6.55 | 3.75 | 1.296 | 480 | 15.2798
|  | May | 39.8 | 9.2 | 4.6 | 35.2 | 1.75 | 24 | 1.5 | 5.8 | 9.05 | 3.75 | 1.296 | 496 | 21.8156
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 1.75 | 24 | 1.5 | 4.6 | 7.85 | 3.75 | 1.296 | 480 | 18.3125
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 1.75 | 24 | 1.5 | 3.55 | 6.8 | 3.75 | 1.296 | 496 | 16.3918
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 1.75 | 24 | 1.5 | 2.55 | 5.8 | 3.75 | 1.296 | 496 | 13.9812
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 1.75 | 24 | 1.5 | 1.75 | 5 | 3.75 | 1.296 | 480 | 11.664
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 1.75 | 24 | 1.5 | 1.25 | 4.5 | 3.75 | 1.296 | 496 | 10.8475
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 1.75 | 24 | 1.5 | -1.25 | 2 | 3.75 | 1.296 | 480 | 4.6656
|  | Dec | 30.1 | 6.7 | 3.35 | 26.75 | 1.75 | 24 | 1.5 | -2.65 | 0.6 | 3.75 | 1.296 | 496 | 1.4463
|  | TLgw-AMD (KWh) | [12 empty] | 128.7122
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 25°C
|  | Jan | 30.2 | 7.9 | 3.95 | 26.25 | 1.75 | 25 | 0.5 | -3.15 | -0.9 | 3.75 | 1.296 | 496 | -2.1695
|  | Feb | 32.2 | 8.7 | 4.35 | 27.85 | 1.75 | 25 | 0.5 | -1.55 | 0.7 | 3.75 | 1.296 | 448 | 1.5241
|  | Mar | 34.9 | 8.9 | 4.45 | 30.45 | 1.75 | 25 | 0.5 | 1.05 | 3.3 | 3.75 | 1.296 | 496 | 7.9548
|  | Apr | 36.8 | 8.2 | 4.1 | 32.7 | 1.75 | 25 | 0.5 | 3.3 | 5.55 | 3.75 | 1.296 | 480 | 12.947
|  | May | 39.8 | 9.2 | 4.6 | 35.2 | 1.75 | 25 | 0.5 | 5.8 | 8.05 | 3.75 | 1.296 | 496 | 19.405
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 1.75 | 25 | 0.5 | 4.6 | 6.85 | 3.75 | 1.296 | 480 | 15.9797
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 1.75 | 25 | 0.5 | 3.55 | 5.8 | 3.75 | 1.296 | 496 | 13.9812
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 1.75 | 25 | 0.5 | 2.55 | 4.8 | 3.75 | 1.296 | 496 | 11.5707
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 1.75 | 25 | 0.5 | 1.75 | 4 | 3.75 | 1.296 | 480 | 9.3312
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 1.75 | 25 | 0.5 | 1.25 | 3.5 | 3.75 | 1.296 | 496 | 8.437
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 1.75 | 25 | 0.5 | -1.25 | 1 | 3.75 | 1.296 | 480 | 2.3328
|  | Dec | 30.1 | 6.7 | 3.35 | 26.75 | 1.75 | 25 | 0.5 | -2.65 | -0.4 | 3.75 | 1.296 | 496 | -0.96422
|  | TLgw-DEL (KWh) | [12 empty] | 100.3298
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 26°C
|  | Jan | 30.2 | 7.9 | 3.95 | 26.25 | 1.75 | 26 | -0.5 | -3.15 | -1.9 | 3.75 | 1.296 | 496 | -4.5801
|  | Feb | 32.2 | 8.7 | 4.35 | 27.85 | 1.75 | 26 | -0.5 | -1.55 | -0.3 | 3.75 | 1.296 | 448 | -0.65318
|  | Mar | 34.9 | 8.9 | 4.45 | 30.45 | 1.75 | 26 | -0.5 | 1.05 | 2.3 | 3.75 | 1.296 | 496 | 5.5443
|  | Apr | 36.8 | 8.2 | 4.1 | 32.7 | 1.75 | 26 | -0.5 | 3.3 | 4.55 | 3.75 | 1.296 | 480 | 10.6142
|  | May | 39.8 | 9.2 | 4.6 | 35.2 | 1.75 | 26 | -0.5 | 5.8 | 7.05 | 3.75 | 1.296 | 496 | 16.9944
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 1.75 | 26 | -0.5 | 4.6 | 5.85 | 3.75 | 1.296 | 480 | 13.6469
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 1.75 | 26 | -0.5 | 3.55 | 4.8 | 3.75 | 1.296 | 496 | 11.5707
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 1.75 | 26 | -0.5 | 2.55 | 3.8 | 3.75 | 1.296 | 496 | 9.1601
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 1.75 | 26 | -0.5 | 1.75 | 3 | 3.75 | 1.296 | 480 | 6.9984
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 1.75 | 26 | -0.5 | 1.25 | 2.5 | 3.75 | 1.296 | 496 | 6.0264
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 1.75 | 26 | -0.5 | -1.25 | 0 | 3.75 | 1.296 | 480 | 0
|  | Dec | 30.1 | 6.7 | 3.35 | 26.75 | 1.75 | 26 | -0.5 | -2.65 | -1.4 | 3.75 | 1.296 | 496 | -3.3748
|  | TLgw-DEL (KWh) | [12 empty] | 71.9474
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 27°C
|  | Jan | 30.2 | 7.9 | 3.95 | 26.25 | 1.75 | 27 | -1.5 | -3.15 | -2.9 | 3.75 | 1.296 | 496 | -6.9906
|  | Feb | 32.2 | 8.7 | 4.35 | 27.85 | 1.75 | 27 | -1.5 | -1.55 | -1.3 | 3.75 | 1.296 | 448 | -2.8305
|  | Mar | 34.9 | 8.9 | 4.45 | 30.45 | 1.75 | 27 | -1.5 | 1.05 | 1.3 | 3.75 | 1.296 | 496 | 3.1337
|  | Apr | 36.8 | 8.2 | 4.1 | 32.7 | 1.75 | 27 | -1.5 | 3.3 | 3.55 | 3.75 | 1.296 | 480 | 8.2814
|  | May | 39.8 | 9.2 | 4.6 | 35.2 | 1.75 | 27 | -1.5 | 5.8 | 6.05 | 3.75 | 1.296 | 496 | 14.5839
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 1.75 | 27 | -1.5 | 4.6 | 4.85 | 3.75 | 1.296 | 480 | 11.3141
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 1.75 | 27 | -1.5 | 3.55 | 3.8 | 3.75 | 1.296 | 496 | 9.1601
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 1.75 | 27 | -1.5 | 2.55 | 2.8 | 3.75 | 1.296 | 496 | 6.7496
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 1.75 | 27 | -1.5 | 1.75 | 2 | 3.75 | 1.296 | 480 | 4.6656
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 1.75 | 27 | -1.5 | 1.25 | 1.5 | 3.75 | 1.296 | 496 | 3.6158
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 1.75 | 27 | -1.5 | -1.25 | -1 | 3.75 | 1.296 | 480 | -2.3328
|  | Dec | 30.1 | 6.7 | 3.35 | 26.75 | 1.75 | 27 | -1.5 | -2.65 | -2.4 | 3.75 | 1.296 | 496 | -5.7853
|  | TLgw-DEL (KWh) | [12 empty] | 43.565
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 28°C
|  | Jan | 30.2 | 7.9 | 3.95 | 26.25 | 1.75 | 28 | -2.5 | -3.15 | -3.9 | 3.75 | 1.296 | 496 | -9.4012
|  | Feb | 32.2 | 8.7 | 4.35 | 27.85 | 1.75 | 28 | -2.5 | -1.55 | -2.3 | 3.75 | 1.296 | 448 | -5.0077
|  | Mar | 34.9 | 8.9 | 4.45 | 30.45 | 1.75 | 28 | -2.5 | 1.05 | 0.3 | 3.75 | 1.296 | 496 | 0.72317
|  | Apr | 36.8 | 8.2 | 4.1 | 32.7 | 1.75 | 28 | -2.5 | 3.3 | 2.55 | 3.75 | 1.296 | 480 | 5.9486
|  | May | 39.8 | 9.2 | 4.6 | 35.2 | 1.75 | 28 | -2.5 | 5.8 | 5.05 | 3.75 | 1.296 | 496 | 12.1733
|  | Jun | 38.4 | 8.8 | 4.4 | 34 | 1.75 | 28 | -2.5 | 4.6 | 3.85 | 3.75 | 1.296 | 480 | 8.9813
|  | Jul | 37 | 8.1 | 4.05 | 32.95 | 1.75 | 28 | -2.5 | 3.55 | 2.8 | 3.75 | 1.296 | 496 | 6.7496
|  | Aug | 35.9 | 7.9 | 3.95 | 31.95 | 1.75 | 28 | -2.5 | 2.55 | 1.8 | 3.75 | 1.296 | 496 | 4.339
|  | Sep | 35 | 7.7 | 3.85 | 31.15 | 1.75 | 28 | -2.5 | 1.75 | 1 | 3.75 | 1.296 | 480 | 2.3328
|  | Oct | 34 | 6.7 | 3.35 | 30.65 | 1.75 | 28 | -2.5 | 1.25 | 0.5 | 3.75 | 1.296 | 496 | 1.2053
|  | Nov | 31.2 | 6.1 | 3.05 | 28.15 | 1.75 | 28 | -2.5 | -1.25 | -2 | 3.75 | 1.296 | 480 | -4.6656
|  | Dec | 30.1 | 6.7 | 3.35 | 26.75 | 1.75 | 28 | -2.5 | -2.65 | -3.4 | 3.75 | 1.296 | 496 | -8.1959
|  | TLgw-DEL (KWh) | [12 empty] | 15.1826
Annual Radiation Thermal Load Through Glass Window
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jan | 0.55 | 0.51 | 94.63 | 1.296 | 496 | 17.0627
|  | Feb | 0.55 | 0.51 | 104.1 | 1.296 | 448 | 16.9538
|  | Mar | 0.55 | 0.51 | 110.41 | 1.296 | 496 | 19.908
|  | Apr | 0.55 | 0.51 | 123.02 | 1.296 | 480 | 21.4662
|  | May | 0.55 | 0.51 | 164.03 | 1.296 | 496 | 29.5762
|  | Jun | 0.55 | 0.51 | 208.2 | 1.296 | 480 | 36.3295
|  | Jul | 0.55 | 0.51 | 173.5 | 1.296 | 496 | 31.2838
|  | Aug | 0.55 | 0.51 | 129.33 | 1.296 | 496 | 23.3195
|  | Sep | 0.55 | 0.51 | 113.56 | 1.296 | 480 | 19.8155
|  | Oct | 0.55 | 0.51 | 104.1 | 1.296 | 496 | 18.7703
|  | Nov | 0.55 | 0.51 | 94.63 | 1.296 | 480 | 16.5123
|  | Dec | 0.55 | 0.51 | 91.48 | 1.296 | 496 | 16.4947
|  | TLrad | [5 empty] | 267.4925
Inflitration Load for Different Setpoint Temperatures
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 30.2 | 22 | 8.2 | 248.5741 | 0.277 | 68.855 | 496 | 34.1521
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 22 | 10.2 | 309.202 | 0.277 | 85.6489 | 448 | 38.3707
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.9 | 22 | 12.9 | 391.0496 | 0.277 | 108.3207 | 496 | 53.7271
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 22 | 14.8 | 448.646 | 0.277 | 124.2749 | 480 | 59.652
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 39.8 | 22 | 17.8 | 539.5878 | 0.277 | 149.4658 | 496 | 74.135
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 22 | 16.4 | 497.1483 | 0.277 | 137.7101 | 480 | 66.1008
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 22 | 15 | 454.7088 | 0.277 | 125.9543 | 496 | 62.4734
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 22 | 13.9 | 421.3635 | 0.277 | 116.7177 | 496 | 57.892
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 22 | 13 | 394.081 | 0.277 | 109.1604 | 480 | 52.397
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 22 | 12 | 363.767 | 0.277 | 100.7635 | 496 | 49.9787
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 22 | 9.2 | 278.8881 | 0.277 | 77.252 | 480 | 37.081
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 30.1 | 22 | 8.1 | 245.5427 | 0.277 | 68.0153 | 496 | 33.7356
|  | Tinf for setpoint 22 degrees C | [11 empty] | 619.6953
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 30.2 | 23 | 7.2 | 218.2602 | 0.277 | 60.4581 | 496 | 29.9872
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 23 | 9.2 | 278.8881 | 0.277 | 77.252 | 448 | 34.6089
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.9 | 23 | 11.9 | 360.7356 | 0.277 | 99.9238 | 496 | 49.5622
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 23 | 13.8 | 418.3321 | 0.277 | 115.878 | 480 | 55.6214
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 39.8 | 23 | 16.8 | 509.2738 | 0.277 | 141.0689 | 496 | 69.9702
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 23 | 15.4 | 466.8344 | 0.277 | 129.3131 | 480 | 62.0703
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 23 | 14 | 424.3949 | 0.277 | 117.5574 | 496 | 58.3085
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 23 | 12.9 | 391.0496 | 0.277 | 108.3207 | 496 | 53.7271
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 23 | 12 | 363.767 | 0.277 | 100.7635 | 480 | 48.3665
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 23 | 11 | 333.4531 | 0.277 | 92.3665 | 496 | 45.8138
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 23 | 8.2 | 248.5741 | 0.277 | 68.855 | 480 | 33.0504
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 30.1 | 23 | 7.1 | 215.2288 | 0.277 | 59.6184 | 496 | 29.5707
|  | Tinf for setpoint 23 degrees C | [11 empty] | 570.6571
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 30.2 | 24 | 6.2 | 187.9463 | 0.277 | 52.0611 | 496 | 25.8223
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 24 | 8.2 | 248.5741 | 0.277 | 68.855 | 448 | 30.8471
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.9 | 24 | 10.9 | 330.4217 | 0.277 | 91.5268 | 496 | 45.3973
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 24 | 12.8 | 388.0182 | 0.277 | 107.481 | 480 | 51.5909
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 39.8 | 24 | 15.8 | 478.9599 | 0.277 | 132.6719 | 496 | 65.8053
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 24 | 14.4 | 436.5204 | 0.277 | 120.9162 | 480 | 58.0398
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 24 | 13 | 394.081 | 0.277 | 109.1604 | 496 | 54.1436
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 24 | 11.9 | 360.7356 | 0.277 | 99.9238 | 496 | 49.5622
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 24 | 11 | 333.4531 | 0.277 | 92.3665 | 480 | 44.3359
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 24 | 10 | 303.1392 | 0.277 | 83.9696 | 496 | 41.6489
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 24 | 7.2 | 218.2602 | 0.277 | 60.4581 | 480 | 29.0199
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 30.1 | 24 | 6.1 | 184.9149 | 0.277 | 51.2214 | 496 | 25.4058
|  | Tinf for setpoint 24 degrees C | [11 empty] | 521.6189
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 30.2 | 25 | 5.2 | 157.6324 | 0.277 | 43.6642 | 496 | 21.6574
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 25 | 7.2 | 218.2602 | 0.277 | 60.4581 | 448 | 27.0852
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.9 | 25 | 9.9 | 300.1078 | 0.277 | 83.1299 | 496 | 41.2324
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 25 | 11.8 | 357.7043 | 0.277 | 99.0841 | 480 | 47.5604
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 39.8 | 25 | 14.8 | 448.646 | 0.277 | 124.2749 | 496 | 61.6404
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 25 | 13.4 | 406.2065 | 0.277 | 112.5192 | 480 | 54.0092
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 25 | 12 | 363.767 | 0.277 | 100.7635 | 496 | 49.9787
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 25 | 10.9 | 330.4217 | 0.277 | 91.5268 | 496 | 45.3973
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 25 | 10 | 303.1392 | 0.277 | 83.9696 | 480 | 40.3054
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 25 | 9 | 272.8253 | 0.277 | 75.5726 | 496 | 37.484
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 25 | 6.2 | 187.9463 | 0.277 | 52.0611 | 480 | 24.9893
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 30.1 | 25 | 5.1 | 154.601 | 0.277 | 42.8245 | 496 | 21.2409
|  | Tinf for setpoint 25 degrees C | [11 empty] | 472.5807
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 30.2 | 26 | 4.2 | 127.3185 | 0.277 | 35.2672 | 496 | 17.4925
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 26 | 6.2 | 187.9463 | 0.277 | 52.0611 | 448 | 23.3234
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.9 | 26 | 8.9 | 269.7939 | 0.277 | 74.7329 | 496 | 37.0675
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 26 | 10.8 | 327.3903 | 0.277 | 90.6871 | 480 | 43.5298
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 39.8 | 26 | 13.8 | 418.3321 | 0.277 | 115.878 | 496 | 57.4755
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 26 | 12.4 | 375.8926 | 0.277 | 104.1223 | 480 | 49.9787
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 26 | 11 | 333.4531 | 0.277 | 92.3665 | 496 | 45.8138
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 26 | 9.9 | 300.1078 | 0.277 | 83.1299 | 496 | 41.2324
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 26 | 9 | 272.8253 | 0.277 | 75.5726 | 480 | 36.2748
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 26 | 8 | 242.5114 | 0.277 | 67.1756 | 496 | 33.3191
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 26 | 5.2 | 157.6324 | 0.277 | 43.6642 | 480 | 20.9588
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 30.1 | 26 | 4.1 | 124.2871 | 0.277 | 34.4275 | 496 | 17.076
|  | Tinf for setpoint 26 degrees C | [11 empty] | 423.5424
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 30.2 | 27 | 3.2 | 97.0045 | 0.277 | 26.8703 | 496 | 13.3276
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 27 | 5.2 | 157.6324 | 0.277 | 43.6642 | 448 | 19.5615
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.9 | 27 | 7.9 | 239.48 | 0.277 | 66.336 | 496 | 32.9026
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 27 | 9.8 | 297.0764 | 0.277 | 82.2902 | 480 | 39.4993
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 39.8 | 27 | 12.8 | 388.0182 | 0.277 | 107.481 | 496 | 53.3106
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 27 | 11.4 | 345.5787 | 0.277 | 95.7253 | 480 | 45.9481
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 27 | 10 | 303.1392 | 0.277 | 83.9696 | 496 | 41.6489
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 27 | 8.9 | 269.7939 | 0.277 | 74.7329 | 496 | 37.0675
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 27 | 8 | 242.5114 | 0.277 | 67.1756 | 480 | 32.2443
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 27 | 7 | 212.1974 | 0.277 | 58.7787 | 496 | 29.1542
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 27 | 4.2 | 127.3185 | 0.277 | 35.2672 | 480 | 16.9283
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 30.1 | 27 | 3.1 | 93.9732 | 0.277 | 26.0306 | 496 | 12.9112
|  | Tinf for setpoint 27 degrees C | [11 empty] | 374.5042
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 30.2 | 28 | 2.2 | 66.6906 | 0.277 | 18.4733 | 496 | 9.1628
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 28 | 4.2 | 127.3185 | 0.277 | 35.2672 | 448 | 15.7997
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.9 | 28 | 6.9 | 209.166 | 0.277 | 57.939 | 496 | 28.7377
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 28 | 8.8 | 266.7625 | 0.277 | 73.8932 | 480 | 35.4687
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 39.8 | 28 | 11.8 | 357.7043 | 0.277 | 99.0841 | 496 | 49.1457
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 38.4 | 28 | 10.4 | 315.2648 | 0.277 | 87.3283 | 480 | 41.9176
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 37 | 28 | 9 | 272.8253 | 0.277 | 75.5726 | 496 | 37.484
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 28 | 7.9 | 239.48 | 0.277 | 66.336 | 496 | 32.9026
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 28 | 7 | 212.1974 | 0.277 | 58.7787 | 480 | 28.2138
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 28 | 6 | 181.8835 | 0.277 | 50.3817 | 496 | 24.9893
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 28 | 3.2 | 97.0045 | 0.277 | 26.8703 | 480 | 12.8977
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 30.1 | 28 | 2.1 | 63.6592 | 0.277 | 17.6336 | 496 | 8.7463
|  | Tinf for setpoint 28 degrees C | [11 empty] | 325.466
Total Internal Load by People
|  | Month | People | SenL/person | CLF | SensL (W) | Latent/Person | LatentL (W) | Total peo L (W) | AC opn hrs | Total PL (KWh)
|  | Jan | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Feb | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 448 | 188.16
|  | Mar | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Apr | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 | 201.6
|  | May | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Jun | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 | 201.6
|  | Jul | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Aug | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Sep | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 | 201.6
|  | Oct | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Nov | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 | 201.6
|  | Dec | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Total Internal Load by People | [8 empty] | 2452.8
Total Internal Heat Load of Lights per Year
|  | No. Bulbs | Watt Rating | bf | Fu | CLF | hrs (6hrs/day) | Tihlig(KWh)
|  | 3 | 60 | 1.24 | 0.66 | 0.8 | 2190 | 258.0906
|  | Total Internal Heat Load of Lights per Year | [5 empty] | 258.0906
Total Internal Heat Load-Equipment
|  | TV Rating W | Hrs /day | Total hrs | Tihe (KWh)
|  | 36 | 5 | 1825 | 65.7
|  | Total load Equipment |  |  | 65.7
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 22 | 185.477 | 267.4925 | 619.6953 | 2452.8 | 258.0906 | 65.7 | 3849.2555
|  | 23 | 157.0946 | 267.4925 | 570.6571 | 2452.8 | 258.0906 | 65.7 | 3771.8349
|  | 24 | 128.7122 | 267.4925 | 521.6189 | 2452.8 | 258.0906 | 65.7 | 3694.4143
|  | 25 | 100.3298 | 267.4925 | 472.5807 | 2452.8 | 258.0906 | 65.7 | 3616.9936
|  | 26 | 71.9474 | 267.4925 | 423.5424 | 2452.8 | 258.0906 | 65.7 | 3539.573
|  | 27 | 43.565 | 267.4925 | 374.5042 | 2452.8 | 258.0906 | 65.7 | 3462.1524
|  | 28 | 15.1826 | 267.4925 | 325.466 | 2452.8 | 258.0906 | 65.7 | 3384.7318

## All Season Dengue Endemic_TH
Balance Point Temperature, Annual Variable Degree Days, Thermal Load of Living Space and Annual Electricity Consumption Calculations for Chennai- Baseline and Solar Electricity Scenarios
|  | Month | [8 empty] | VCDDmth | AC hrs/24 hrs (fAC) | Conv (24/1000) KWh |  |  | Annual VCDD |  |  |  | Annual VCDD |  |  |  | Annual VCDD |  | All Other Heat Loads | BE+Other Loads | 10%SF |  | EER | Elec. Cons. |  | LDRZ Setpoint Adjsuted Preference %
|  | Jan | 22 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9605 | 243.1 | [21 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Feb | 22 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9434 | 282.8 | [21 empty] | 22 | 16 | 0.34783
|  | Mar | 22 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9319 | 351.7 | [21 empty] | 23 | 10 | 0.21739
|  | Apr | 22 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.909 | 364.1 | [21 empty] | 24 | 20 | 0.43478
|  | May | 22 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8347 | 353.8 | [22 empty] | 46
|  | Jun | 22 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.7545 | 329
|  | July | 22 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8175 | 293.1
|  | Aug | 22 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8976 | 316.7
|  | Sep | 22 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9262 | 289.8
|  | Oct | 22 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9434 | 317.5
|  | Nov | 22 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9605 | 320.3
|  | Dec | 22 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9662 | 286.1
|  | Annual VCDD | [8 empty] | 3748 | 0.66667 | 0.024 | 3.59 | 12.96 | 3748 | 2790.0952 | 3.94 | 12.96 | 3748 | 3062.11 | 2.13 | 41.904 | 3748 | 5352.475 | 3838.5137 | 15043.1939 | 1504.3194 | 16547.5133 | 3.1 | 5338 | 22
|  | Month | [8 empty] | VCDDmth
|  | Jan | 23 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9605 | 212.2
|  | Feb | 23 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9434 | 254.8
|  | Mar | 23 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9319 | 320.7
|  | Apr | 23 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.909 | 334.1
|  | May | 23 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8347 | 322.8
|  | Jun | 23 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.7545 | 299
|  | July | 23 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8175 | 262.1
|  | Aug | 23 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8976 | 285.7
|  | Sep | 23 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9262 | 259.8
|  | Oct | 23 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9434 | 286.5
|  | Nov | 23 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9605 | 290.3
|  | Dec | 23 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9662 | 255.1
|  | Annual VCDD | [8 empty] | 3383.1 | 0.66667 | 0.024 | 3.59 | 12.96 | 3383.1 | 2518.4554 | 3.94 | 12.96 | 3383.1 | 2763.9873 | 2.13 | 41.904 | 3383.1 | 4831.3656 | 3761.0931 | 13874.9014 | 1387.4901 | 15262.3916 | 3.1 | 4923 | 23
|  | Month | [8 empty] | VCDDmth
|  | Jan | 24 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9605 | 181.9
|  | Feb | 24 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9434 | 226.8
|  | Mar | 24 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9319 | 289.7
|  | Apr | 24 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.909 | 304.1
|  | May | 24 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8347 | 291.8
|  | Jun | 24 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.7545 | 269
|  | Jul | 24 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8175 | 231.1
|  | Aug | 24 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8976 | 254.7
|  | Sep | 24 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9262 | 229.8
|  | Oct | 24 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9434 | 255.5
|  | Nov | 24 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9605 | 260.3
|  | Dec | 24 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9662 | 224.1
|  | Annual VCDD | [8 empty] | 3018.8 | 0.66667 | 0.024 | 3.59 | 12.96 | 3018.8 | 2247.2623 | 3.94 | 12.96 | 3018.8 | 2466.3548 | 2.13 | 41.904 | 3018.8 | 4311.113 | 3683.6725 | 12708.4026 | 1270.8403 | 13979.2429 | 3.1 | 4509 | 24 | MDRZ Setpoint Adjsuted Preference %
|  | Avg Annual VCDD Based on Consumer Setpoint Prefreneces for Bangkok, Thailand for Low Dengue Risk Zone (LDRZ) | [28 empty] | 4887.3478
|  | Month | [8 empty] | VCDDmth | [21 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Jan | 25 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9605 | 151.8 | [21 empty] | 25 | 12 | 100
|  | Feb | 25 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9434 | 198.8
|  | Mar | 25 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9319 | 258.7
|  | Apr | 25 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.909 | 274.1
|  | May | 25 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8347 | 260.8
|  | Jun | 25 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.7545 | 239
|  | Jul | 25 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8175 | 200.1
|  | Aug | 25 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8976 | 223.7
|  | Sep | 25 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9262 | 199.8
|  | Oct | 25 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9434 | 224.5
|  | Nov | 25 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9605 | 230.3
|  | Dec | 25 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9662 | 193.2
|  | Annual VCDD | [8 empty] | 2654.8 | 0.66667 | 0.024 | 3.59 | 12.96 | 2654.8 | 1976.2926 | 3.94 | 12.96 | 2654.8 | 2168.9674 | 2.13 | 41.904 | 2654.8 | 3791.2889 | 3606.2519 | 11542.8007 | 1154.2801 | 12697.0808 | 3.1 | 4096
|  | Avg Annual VCDD Based on Consumer Setpoint Prefreneces for Bangkok, Thailand for Moderate Dengue Risk Zone (MDRZ) | [28 empty] | 4096 | 25
|  | Month | [8 empty] | VCDDmth
|  | Jan | 26 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9605 | 123.2
|  | Feb | 26 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9434 | 170.8
|  | Mar | 26 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9319 | 227.7
|  | Apr | 26 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.909 | 244.1
|  | May | 26 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8347 | 229.8
|  | Jun | 26 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.7545 | 209
|  | July | 26 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8175 | 169.1
|  | Aug | 26 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8976 | 192.7
|  | Sep | 26 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9262 | 169.8
|  | Oct | 26 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9434 | 193.5
|  | Nov | 26 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9605 | 200.3
|  | Dec | 26 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9662 | 162.7
|  | Annual VCDD | [8 empty] | 2292.7 | 0.66667 | 0.024 | 3.59 | 12.96 | 2292.7 | 1706.7372 | 3.94 | 12.96 | 2292.7 | 1873.1322 | 2.13 | 41.904 | 2292.7 | 3274.1781 | 3528.8313 | 10382.8788 | 1038.2879 | 11421.1667 | 3.1 | 3684 | 26
|  | Month | [8 empty] | VCDDmth | [21 empty] | HDRZ Setpoint Adjsuted Preference %
|  | Jan | 27 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9605 | 97.4 | [21 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Feb | 27 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9434 | 143 | [21 empty] | 26 | 10 | 0.5
|  | Mar | 27 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9319 | 196.7 | [21 empty] | 27 | 8 | 0.4
|  | Apr | 27 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.909 | 214.1 | [21 empty] | 28 | 2 | 0.1
|  | May | 27 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8347 | 198.8 | [22 empty] | 20
|  | Jun | 27 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.7545 | 179
|  | Jul | 27 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8175 | 138.3
|  | Aug | 27 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8976 | 162
|  | Sep | 27 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9262 | 139.8
|  | Oct | 27 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9434 | 162.5
|  | Nov | 27 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9605 | 170.4
|  | Dec | 27 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9662 | 133.1
|  | Annual VCDD | [8 empty] | 1935.1 | 0.66667 | 0.024 | 3.59 | 12.96 | 1935.1 | 1440.5318 | 3.94 | 12.96 | 1935.1 | 1580.9736 | 2.13 | 41.904 | 1935.1 | 2763.4937 | 3451.4106 | 9236.4097 | 923.641 | 10160.0507 | 3.1 | 3277 | 27
|  | Month | [8 empty] | VCDDmth
|  | Jan | 28 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9605 | 75.3
|  | Feb | 28 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9434 | 116.1
|  | Mar | 28 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9319 | 165.8
|  | Apr | 28 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.909 | 184.1
|  | May | 28 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8347 | 168.2
|  | Jun | 28 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.7545 | 149
|  | Jul | 28 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8175 | 107.8
|  | Aug | 28 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8976 | 132.2
|  | Sep | 28 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9262 | 110.3
|  | Oct | 28 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9434 | 131.9
|  | Nov | 28 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9605 | 140.8
|  | Dec | 28 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9662 | 105.4
|  | Annual VCDD | [8 empty] | 1586.9 | 0.66667 | 0.024 | 3.59 | 12.96 | 1586.9 | 1181.3239 | 3.94 | 12.96 | 1586.9 | 1296.4948 | 2.13 | 41.904 | 1586.9 | 2266.2334 | 3373.99 | 8118.042 | 811.8042 | 8929.8462 | 3.1 | 2881 | 28
|  | Avg Annual VCDD Based on Consumer Setpoint Prefreneces for Bangkok, Thailand for High Dengue Risk Zone (HDRZ) | [28 empty] | 3441
CLTDgw-avg (°C) for AC Opn hrs. |  | Thermal Conductive Load (TLgw-x) Calculated for Three Climate Zones
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 22°C
AC Opn hrs. | CLTDgw (°C) | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
00.00-01.00 | 1 | Jan | 33.3 | 8.1 | 4.05 | 29.25 | 1.75 | 22 | 3.5 | -0.15 | 5.1 | 3.75 | 1.296 | 496 | 12.2939
01.00-02.00 | 1 | Feb | 34.1 | 7.4 | 3.7 | 30.4 | 1.75 | 22 | 3.5 | 1 | 6.25 | 3.75 | 1.296 | 448 | 13.608
02.00-03.00 | 0 | Mar | 35.2 | 6.9 | 3.45 | 31.75 | 1.75 | 22 | 3.5 | 2.35 | 7.6 | 3.75 | 1.296 | 496 | 18.3203
03.00-04.00 | -1 | Apr | 36.4 | 7.1 | 3.55 | 32.85 | 1.75 | 22 | 3.5 | 3.45 | 8.7 | 3.75 | 1.296 | 480 | 20.2954
04.00-05.00 | -1 | May | 36.1 | 6.7 | 3.35 | 32.75 | 1.75 | 22 | 3.5 | 3.35 | 8.6 | 3.75 | 1.296 | 496 | 20.7308
05.00-06.00 | -1 | Jun | 34.6 | 6.2 | 3.1 | 31.5 | 1.75 | 22 | 3.5 | 2.1 | 7.35 | 3.75 | 1.296 | 480 | 17.1461
06.00-07.00 | -1 | Jul | 34 | 5.8 | 2.9 | 31.1 | 1.75 | 22 | 3.5 | 1.7 | 6.95 | 3.75 | 1.296 | 496 | 16.7534
07.00-08.00 | -1 | Aug | 33.8 | 5.9 | 2.95 | 30.85 | 1.75 | 22 | 3.5 | 1.45 | 6.7 | 3.75 | 1.296 | 496 | 16.1508
08.00-09.00 | 0 | Sep | 33.6 | 6.2 | 3.1 | 30.5 | 1.75 | 22 | 3.5 | 1.1 | 6.35 | 3.75 | 1.296 | 480 | 14.8133
17.00-18.00 | 7 | Oct | 33.7 | 6.4 | 3.2 | 30.5 | 1.75 | 22 | 3.5 | 1.1 | 6.35 | 3.75 | 1.296 | 496 | 15.3071
18.00-19.00 | 7 | Nov | 33.5 | 6.9 | 3.45 | 30.05 | 1.75 | 22 | 3.5 | 0.65 | 5.9 | 3.75 | 1.296 | 480 | 13.7635
19.00-20.00 | 6 | Dec | 33.2 | 7.7 | 3.85 | 29.35 | 1.75 | 22 | 3.5 | -0.05 | 5.2 | 3.75 | 1.296 | 496 | 12.5349
20.00-21.00 | 4 | TLgw-CHN (KWh) | [12 empty] | 191.7173
21.00-22.00 | 3 | Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 23°C
22.00-23.00 | 2 | Jan | 33.3 | 8.1 | 4.05 | 29.25 | 1.75 | 23 | 2.5 | -0.15 | 4.1 | 3.75 | 1.296 | 496 | 9.8833
23.00-00.00 | 2 | Feb | 34.1 | 7.4 | 3.7 | 30.4 | 1.75 | 23 | 2.5 | 1 | 5.25 | 3.75 | 1.296 | 448 | 11.4307
CLTDgw-avg (°C) | 1.75 | Mar | 35.2 | 6.9 | 3.45 | 31.75 | 1.75 | 23 | 2.5 | 2.35 | 6.6 | 3.75 | 1.296 | 496 | 15.9097
|  | Apr | 36.4 | 7.1 | 3.55 | 32.85 | 1.75 | 23 | 2.5 | 3.45 | 7.7 | 3.75 | 1.296 | 480 | 17.9626
|  | May | 36.1 | 6.7 | 3.35 | 32.75 | 1.75 | 23 | 2.5 | 3.35 | 7.6 | 3.75 | 1.296 | 496 | 18.3203
|  | Jun | 34.6 | 6.2 | 3.1 | 31.5 | 1.75 | 23 | 2.5 | 2.1 | 6.35 | 3.75 | 1.296 | 480 | 14.8133
|  | Jul | 34 | 5.8 | 2.9 | 31.1 | 1.75 | 23 | 2.5 | 1.7 | 5.95 | 3.75 | 1.296 | 496 | 14.3428
|  | Aug | 33.8 | 5.9 | 2.95 | 30.85 | 1.75 | 23 | 2.5 | 1.45 | 5.7 | 3.75 | 1.296 | 496 | 13.7402
|  | Sep | 33.6 | 6.2 | 3.1 | 30.5 | 1.75 | 23 | 2.5 | 1.1 | 5.35 | 3.75 | 1.296 | 480 | 12.4805
|  | Oct | 33.7 | 6.4 | 3.2 | 30.5 | 1.75 | 23 | 2.5 | 1.1 | 5.35 | 3.75 | 1.296 | 496 | 12.8965
|  | Nov | 33.5 | 6.9 | 3.45 | 30.05 | 1.75 | 23 | 2.5 | 0.65 | 4.9 | 3.75 | 1.296 | 480 | 11.4307
|  | Dec | 33.2 | 7.7 | 3.85 | 29.35 | 1.75 | 23 | 2.5 | -0.05 | 4.2 | 3.75 | 1.296 | 496 | 10.1244
|  | TLgw-CHN (KWh) | [12 empty] | 163.3349
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 24°C
|  | Jan | 33.3 | 8.1 | 4.05 | 29.25 | 1.75 | 24 | 1.5 | -0.15 | 3.1 | 3.75 | 1.296 | 496 | 7.4727
|  | Feb | 34.1 | 7.4 | 3.7 | 30.4 | 1.75 | 24 | 1.5 | 1 | 4.25 | 3.75 | 1.296 | 448 | 9.2534
|  | Mar | 35.2 | 6.9 | 3.45 | 31.75 | 1.75 | 24 | 1.5 | 2.35 | 5.6 | 3.75 | 1.296 | 496 | 13.4991
|  | Apr | 36.4 | 7.1 | 3.55 | 32.85 | 1.75 | 24 | 1.5 | 3.45 | 6.7 | 3.75 | 1.296 | 480 | 15.6298
|  | May | 36.1 | 6.7 | 3.35 | 32.75 | 1.75 | 24 | 1.5 | 3.35 | 6.6 | 3.75 | 1.296 | 496 | 15.9097
|  | Jun | 34.6 | 6.2 | 3.1 | 31.5 | 1.75 | 24 | 1.5 | 2.1 | 5.35 | 3.75 | 1.296 | 480 | 12.4805
|  | Jul | 34 | 5.8 | 2.9 | 31.1 | 1.75 | 24 | 1.5 | 1.7 | 4.95 | 3.75 | 1.296 | 496 | 11.9323
|  | Aug | 33.8 | 5.9 | 2.95 | 30.85 | 1.75 | 24 | 1.5 | 1.45 | 4.7 | 3.75 | 1.296 | 496 | 11.3296
|  | Sep | 33.6 | 6.2 | 3.1 | 30.5 | 1.75 | 24 | 1.5 | 1.1 | 4.35 | 3.75 | 1.296 | 480 | 10.1477
|  | Oct | 33.7 | 6.4 | 3.2 | 30.5 | 1.75 | 24 | 1.5 | 1.1 | 4.35 | 3.75 | 1.296 | 496 | 10.4859
|  | Nov | 33.5 | 6.9 | 3.45 | 30.05 | 1.75 | 24 | 1.5 | 0.65 | 3.9 | 3.75 | 1.296 | 480 | 9.0979
|  | Dec | 33.2 | 7.7 | 3.85 | 29.35 | 1.75 | 24 | 1.5 | -0.05 | 3.2 | 3.75 | 1.296 | 496 | 7.7138
|  | TLgw-AMD (KWh) | [12 empty] | 134.9525
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 25°C
|  | Jan | 33.3 | 8.1 | 4.05 | 29.25 | 1.75 | 25 | 0.5 | -0.15 | 2.1 | 3.75 | 1.296 | 496 | 5.0622
|  | Feb | 34.1 | 7.4 | 3.7 | 30.4 | 1.75 | 25 | 0.5 | 1 | 3.25 | 3.75 | 1.296 | 448 | 7.0762
|  | Mar | 35.2 | 6.9 | 3.45 | 31.75 | 1.75 | 25 | 0.5 | 2.35 | 4.6 | 3.75 | 1.296 | 496 | 11.0886
|  | Apr | 36.4 | 7.1 | 3.55 | 32.85 | 1.75 | 25 | 0.5 | 3.45 | 5.7 | 3.75 | 1.296 | 480 | 13.297
|  | May | 36.1 | 6.7 | 3.35 | 32.75 | 1.75 | 25 | 0.5 | 3.35 | 5.6 | 3.75 | 1.296 | 496 | 13.4991
|  | Jun | 34.6 | 6.2 | 3.1 | 31.5 | 1.75 | 25 | 0.5 | 2.1 | 4.35 | 3.75 | 1.296 | 480 | 10.1477
|  | Jul | 34 | 5.8 | 2.9 | 31.1 | 1.75 | 25 | 0.5 | 1.7 | 3.95 | 3.75 | 1.296 | 496 | 9.5217
|  | Aug | 33.8 | 5.9 | 2.95 | 30.85 | 1.75 | 25 | 0.5 | 1.45 | 3.7 | 3.75 | 1.296 | 496 | 8.9191
|  | Sep | 33.6 | 6.2 | 3.1 | 30.5 | 1.75 | 25 | 0.5 | 1.1 | 3.35 | 3.75 | 1.296 | 480 | 7.8149
|  | Oct | 33.7 | 6.4 | 3.2 | 30.5 | 1.75 | 25 | 0.5 | 1.1 | 3.35 | 3.75 | 1.296 | 496 | 8.0754
|  | Nov | 33.5 | 6.9 | 3.45 | 30.05 | 1.75 | 25 | 0.5 | 0.65 | 2.9 | 3.75 | 1.296 | 480 | 6.7651
|  | Dec | 33.2 | 7.7 | 3.85 | 29.35 | 1.75 | 25 | 0.5 | -0.05 | 2.2 | 3.75 | 1.296 | 496 | 5.3032
|  | TLgw-DEL (KWh) | [12 empty] | 106.5701
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 26°C
|  | Jan | 33.3 | 8.1 | 4.05 | 29.25 | 1.75 | 26 | -0.5 | -0.15 | 1.1 | 3.75 | 1.296 | 496 | 2.6516
|  | Feb | 34.1 | 7.4 | 3.7 | 30.4 | 1.75 | 26 | -0.5 | 1 | 2.25 | 3.75 | 1.296 | 448 | 4.8989
|  | Mar | 35.2 | 6.9 | 3.45 | 31.75 | 1.75 | 26 | -0.5 | 2.35 | 3.6 | 3.75 | 1.296 | 496 | 8.678
|  | Apr | 36.4 | 7.1 | 3.55 | 32.85 | 1.75 | 26 | -0.5 | 3.45 | 4.7 | 3.75 | 1.296 | 480 | 10.9642
|  | May | 36.1 | 6.7 | 3.35 | 32.75 | 1.75 | 26 | -0.5 | 3.35 | 4.6 | 3.75 | 1.296 | 496 | 11.0886
|  | Jun | 34.6 | 6.2 | 3.1 | 31.5 | 1.75 | 26 | -0.5 | 2.1 | 3.35 | 3.75 | 1.296 | 480 | 7.8149
|  | Jul | 34 | 5.8 | 2.9 | 31.1 | 1.75 | 26 | -0.5 | 1.7 | 2.95 | 3.75 | 1.296 | 496 | 7.1112
|  | Aug | 33.8 | 5.9 | 2.95 | 30.85 | 1.75 | 26 | -0.5 | 1.45 | 2.7 | 3.75 | 1.296 | 496 | 6.5085
|  | Sep | 33.6 | 6.2 | 3.1 | 30.5 | 1.75 | 26 | -0.5 | 1.1 | 2.35 | 3.75 | 1.296 | 480 | 5.4821
|  | Oct | 33.7 | 6.4 | 3.2 | 30.5 | 1.75 | 26 | -0.5 | 1.1 | 2.35 | 3.75 | 1.296 | 496 | 5.6648
|  | Nov | 33.5 | 6.9 | 3.45 | 30.05 | 1.75 | 26 | -0.5 | 0.65 | 1.9 | 3.75 | 1.296 | 480 | 4.4323
|  | Dec | 33.2 | 7.7 | 3.85 | 29.35 | 1.75 | 26 | -0.5 | -0.05 | 1.2 | 3.75 | 1.296 | 496 | 2.8927
|  | TLgw-DEL (KWh) | [12 empty] | 78.1877
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 27°C
|  | Jan | 33.3 | 8.1 | 4.05 | 29.25 | 1.75 | 27 | -1.5 | -0.15 | 0.1 | 3.75 | 1.296 | 496 | 0.24106
|  | Feb | 34.1 | 7.4 | 3.7 | 30.4 | 1.75 | 27 | -1.5 | 1 | 1.25 | 3.75 | 1.296 | 448 | 2.7216
|  | Mar | 35.2 | 6.9 | 3.45 | 31.75 | 1.75 | 27 | -1.5 | 2.35 | 2.6 | 3.75 | 1.296 | 496 | 6.2675
|  | Apr | 36.4 | 7.1 | 3.55 | 32.85 | 1.75 | 27 | -1.5 | 3.45 | 3.7 | 3.75 | 1.296 | 480 | 8.6314
|  | May | 36.1 | 6.7 | 3.35 | 32.75 | 1.75 | 27 | -1.5 | 3.35 | 3.6 | 3.75 | 1.296 | 496 | 8.678
|  | Jun | 34.6 | 6.2 | 3.1 | 31.5 | 1.75 | 27 | -1.5 | 2.1 | 2.35 | 3.75 | 1.296 | 480 | 5.4821
|  | Jul | 34 | 5.8 | 2.9 | 31.1 | 1.75 | 27 | -1.5 | 1.7 | 1.95 | 3.75 | 1.296 | 496 | 4.7006
|  | Aug | 33.8 | 5.9 | 2.95 | 30.85 | 1.75 | 27 | -1.5 | 1.45 | 1.7 | 3.75 | 1.296 | 496 | 4.098
|  | Sep | 33.6 | 6.2 | 3.1 | 30.5 | 1.75 | 27 | -1.5 | 1.1 | 1.35 | 3.75 | 1.296 | 480 | 3.1493
|  | Oct | 33.7 | 6.4 | 3.2 | 30.5 | 1.75 | 27 | -1.5 | 1.1 | 1.35 | 3.75 | 1.296 | 496 | 3.2543
|  | Nov | 33.5 | 6.9 | 3.45 | 30.05 | 1.75 | 27 | -1.5 | 0.65 | 0.9 | 3.75 | 1.296 | 480 | 2.0995
|  | Dec | 33.2 | 7.7 | 3.85 | 29.35 | 1.75 | 27 | -1.5 | -0.05 | 0.2 | 3.75 | 1.296 | 496 | 0.48211
|  | TLgw-DEL (KWh) | [12 empty] | 49.8053
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 28°C
|  | Jan | 33.3 | 8.1 | 4.05 | 29.25 | 1.75 | 28 | -2.5 | -0.15 | -0.9 | 3.75 | 1.296 | 496 | -2.1695
|  | Feb | 34.1 | 7.4 | 3.7 | 30.4 | 1.75 | 28 | -2.5 | 1 | 0.25 | 3.75 | 1.296 | 448 | 0.54432
|  | Mar | 35.2 | 6.9 | 3.45 | 31.75 | 1.75 | 28 | -2.5 | 2.35 | 1.6 | 3.75 | 1.296 | 496 | 3.8569
|  | Apr | 36.4 | 7.1 | 3.55 | 32.85 | 1.75 | 28 | -2.5 | 3.45 | 2.7 | 3.75 | 1.296 | 480 | 6.2986
|  | May | 36.1 | 6.7 | 3.35 | 32.75 | 1.75 | 28 | -2.5 | 3.35 | 2.6 | 3.75 | 1.296 | 496 | 6.2675
|  | Jun | 34.6 | 6.2 | 3.1 | 31.5 | 1.75 | 28 | -2.5 | 2.1 | 1.35 | 3.75 | 1.296 | 480 | 3.1493
|  | Jul | 34 | 5.8 | 2.9 | 31.1 | 1.75 | 28 | -2.5 | 1.7 | 0.95 | 3.75 | 1.296 | 496 | 2.29
|  | Aug | 33.8 | 5.9 | 2.95 | 30.85 | 1.75 | 28 | -2.5 | 1.45 | 0.7 | 3.75 | 1.296 | 496 | 1.6874
|  | Sep | 33.6 | 6.2 | 3.1 | 30.5 | 1.75 | 28 | -2.5 | 1.1 | 0.35 | 3.75 | 1.296 | 480 | 0.81648
|  | Oct | 33.7 | 6.4 | 3.2 | 30.5 | 1.75 | 28 | -2.5 | 1.1 | 0.35 | 3.75 | 1.296 | 496 | 0.8437
|  | Nov | 33.5 | 6.9 | 3.45 | 30.05 | 1.75 | 28 | -2.5 | 0.65 | -0.1 | 3.75 | 1.296 | 480 | -0.23328
|  | Dec | 33.2 | 7.7 | 3.85 | 29.35 | 1.75 | 28 | -2.5 | -0.05 | -0.8 | 3.75 | 1.296 | 496 | -1.9284
|  | TLgw-DEL (KWh) | [12 empty] | 21.4229
Annual Radiation Thermal Load Through Glass Window
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jan | 0.55 | 0.51 | 94.63 | 1.296 | 496 | 17.0627
|  | Feb | 0.55 | 0.51 | 104.1 | 1.296 | 448 | 16.9538
|  | Mar | 0.55 | 0.51 | 110.41 | 1.296 | 496 | 19.908
|  | Apr | 0.55 | 0.51 | 123.02 | 1.296 | 480 | 21.4662
|  | May | 0.55 | 0.51 | 164.03 | 1.296 | 496 | 29.5762
|  | Jun | 0.55 | 0.51 | 208.2 | 1.296 | 480 | 36.3295
|  | Jul | 0.55 | 0.51 | 173.5 | 1.296 | 496 | 31.2838
|  | Aug | 0.55 | 0.51 | 129.33 | 1.296 | 496 | 23.3195
|  | Sep | 0.55 | 0.51 | 113.56 | 1.296 | 480 | 19.8155
|  | Oct | 0.55 | 0.51 | 104.1 | 1.296 | 496 | 18.7703
|  | Nov | 0.55 | 0.51 | 94.63 | 1.296 | 480 | 16.5123
|  | Dec | 0.55 | 0.51 | 91.48 | 1.296 | 496 | 16.4947
|  | TLrad | [5 empty] | 267.4925
Inflitration Load for Different Setpoint Temperatures
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.3 | 22 | 11.3 | 342.5473 | 0.277 | 94.8856 | 496 | 47.0633
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 22 | 12.1 | 366.7984 | 0.277 | 101.6032 | 448 | 45.5182
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 22 | 13.2 | 400.1437 | 0.277 | 110.8398 | 496 | 54.9765
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.4 | 22 | 14.4 | 436.5204 | 0.277 | 120.9162 | 480 | 58.0398
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 22 | 14.1 | 427.4263 | 0.277 | 118.3971 | 496 | 58.7249
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 22 | 12.6 | 381.9554 | 0.277 | 105.8016 | 480 | 50.7848
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 22 | 12 | 363.767 | 0.277 | 100.7635 | 496 | 49.9787
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 22 | 11.8 | 357.7043 | 0.277 | 99.0841 | 496 | 49.1457
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.6 | 22 | 11.6 | 351.6415 | 0.277 | 97.4047 | 480 | 46.7542
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.7 | 22 | 11.7 | 354.6729 | 0.277 | 98.2444 | 496 | 48.7292
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.5 | 22 | 11.5 | 348.6101 | 0.277 | 96.565 | 480 | 46.3512
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 22 | 11.2 | 339.5159 | 0.277 | 94.0459 | 496 | 46.6468
|  | Tinf for setpoint 22 degrees C | [11 empty] | 602.7133
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.3 | 23 | 10.3 | 312.2334 | 0.277 | 86.4886 | 496 | 42.8984
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 23 | 11.1 | 336.4845 | 0.277 | 93.2062 | 448 | 41.7564
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 23 | 12.2 | 369.8298 | 0.277 | 102.4429 | 496 | 50.8117
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.4 | 23 | 13.4 | 406.2065 | 0.277 | 112.5192 | 480 | 54.0092
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 23 | 13.1 | 397.1123 | 0.277 | 110.0001 | 496 | 54.5601
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 23 | 11.6 | 351.6415 | 0.277 | 97.4047 | 480 | 46.7542
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 23 | 11 | 333.4531 | 0.277 | 92.3665 | 496 | 45.8138
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 23 | 10.8 | 327.3903 | 0.277 | 90.6871 | 496 | 44.9808
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.6 | 23 | 10.6 | 321.3275 | 0.277 | 89.0077 | 480 | 42.7237
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.7 | 23 | 10.7 | 324.3589 | 0.277 | 89.8474 | 496 | 44.5643
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.5 | 23 | 10.5 | 318.2962 | 0.277 | 88.168 | 480 | 42.3207
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 23 | 10.2 | 309.202 | 0.277 | 85.6489 | 496 | 42.4819
|  | Tinf for setpoint 23 degrees C | [11 empty] | 553.6751
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.3 | 24 | 9.3 | 281.9195 | 0.277 | 78.0917 | 496 | 38.7335
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 24 | 10.1 | 306.1706 | 0.277 | 84.8093 | 448 | 37.9945
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 24 | 11.2 | 339.5159 | 0.277 | 94.0459 | 496 | 46.6468
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.4 | 24 | 12.4 | 375.8926 | 0.277 | 104.1223 | 480 | 49.9787
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 24 | 12.1 | 366.7984 | 0.277 | 101.6032 | 496 | 50.3952
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 24 | 10.6 | 321.3275 | 0.277 | 89.0077 | 480 | 42.7237
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 24 | 10 | 303.1392 | 0.277 | 83.9696 | 496 | 41.6489
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 24 | 9.8 | 297.0764 | 0.277 | 82.2902 | 496 | 40.8159
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.6 | 24 | 9.6 | 291.0136 | 0.277 | 80.6108 | 480 | 38.6932
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.7 | 24 | 9.7 | 294.045 | 0.277 | 81.4505 | 496 | 40.3994
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.5 | 24 | 9.5 | 287.9822 | 0.277 | 79.7711 | 480 | 38.2901
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 24 | 9.2 | 278.8881 | 0.277 | 77.252 | 496 | 38.317
|  | Tinf for setpoint 24 degrees C | [11 empty] | 504.6369
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.3 | 25 | 8.3 | 251.6055 | 0.277 | 69.6947 | 496 | 34.5686
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 25 | 9.1 | 275.8567 | 0.277 | 76.4123 | 448 | 34.2327
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 25 | 10.2 | 309.202 | 0.277 | 85.6489 | 496 | 42.4819
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.4 | 25 | 11.4 | 345.5787 | 0.277 | 95.7253 | 480 | 45.9481
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 25 | 11.1 | 336.4845 | 0.277 | 93.2062 | 496 | 46.2303
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 25 | 9.6 | 291.0136 | 0.277 | 80.6108 | 480 | 38.6932
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 25 | 9 | 272.8253 | 0.277 | 75.5726 | 496 | 37.484
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 25 | 8.8 | 266.7625 | 0.277 | 73.8932 | 496 | 36.651
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.6 | 25 | 8.6 | 260.6997 | 0.277 | 72.2138 | 480 | 34.6626
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.7 | 25 | 8.7 | 263.7311 | 0.277 | 73.0535 | 496 | 36.2345
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.5 | 25 | 8.5 | 257.6683 | 0.277 | 71.3741 | 480 | 34.2596
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 25 | 8.2 | 248.5741 | 0.277 | 68.855 | 496 | 34.1521
|  | Tinf for setpoint 25 degrees C | [11 empty] | 455.5987
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.3 | 26 | 7.3 | 221.2916 | 0.277 | 61.2978 | 496 | 30.4037
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 26 | 8.1 | 245.5427 | 0.277 | 68.0153 | 448 | 30.4709
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 26 | 9.2 | 278.8881 | 0.277 | 77.252 | 496 | 38.317
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.4 | 26 | 10.4 | 315.2648 | 0.277 | 87.3283 | 480 | 41.9176
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 26 | 10.1 | 306.1706 | 0.277 | 84.8093 | 496 | 42.0654
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 26 | 8.6 | 260.6997 | 0.277 | 72.2138 | 480 | 34.6626
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 26 | 8 | 242.5114 | 0.277 | 67.1756 | 496 | 33.3191
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 26 | 7.8 | 236.4486 | 0.277 | 65.4963 | 496 | 32.4861
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.6 | 26 | 7.6 | 230.3858 | 0.277 | 63.8169 | 480 | 30.6321
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.7 | 26 | 7.7 | 233.4172 | 0.277 | 64.6566 | 496 | 32.0697
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.5 | 26 | 7.5 | 227.3544 | 0.277 | 62.9772 | 480 | 30.229
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 26 | 7.2 | 218.2602 | 0.277 | 60.4581 | 496 | 29.9872
|  | Tinf for setpoint 26 degrees C | [11 empty] | 406.5604
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.3 | 27 | 6.3 | 190.9777 | 0.277 | 52.9008 | 496 | 26.2388
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 27 | 7.1 | 215.2288 | 0.277 | 59.6184 | 448 | 26.709
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 27 | 8.2 | 248.5741 | 0.277 | 68.855 | 496 | 34.1521
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.4 | 27 | 9.4 | 284.9508 | 0.277 | 78.9314 | 480 | 37.8871
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 27 | 9.1 | 275.8567 | 0.277 | 76.4123 | 496 | 37.9005
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 27 | 7.6 | 230.3858 | 0.277 | 63.8169 | 480 | 30.6321
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 27 | 7 | 212.1974 | 0.277 | 58.7787 | 496 | 29.1542
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 27 | 6.8 | 206.1347 | 0.277 | 57.0993 | 496 | 28.3213
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.6 | 27 | 6.6 | 200.0719 | 0.277 | 55.4199 | 480 | 26.6016
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.7 | 27 | 6.7 | 203.1033 | 0.277 | 56.2596 | 496 | 27.9048
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.5 | 27 | 6.5 | 197.0405 | 0.277 | 54.5802 | 480 | 26.1985
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 27 | 6.2 | 187.9463 | 0.277 | 52.0611 | 496 | 25.8223
|  | Tinf for setpoint 27 degrees C | [11 empty] | 357.5222
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.3 | 28 | 5.3 | 160.6638 | 0.277 | 44.5039 | 496 | 22.0739
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 28 | 6.1 | 184.9149 | 0.277 | 51.2214 | 448 | 22.9472
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35.2 | 28 | 7.2 | 218.2602 | 0.277 | 60.4581 | 496 | 29.9872
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.4 | 28 | 8.4 | 254.6369 | 0.277 | 70.5344 | 480 | 33.8565
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 36.1 | 28 | 8.1 | 245.5427 | 0.277 | 68.0153 | 496 | 33.7356
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 28 | 6.6 | 200.0719 | 0.277 | 55.4199 | 480 | 26.6016
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 28 | 6 | 181.8835 | 0.277 | 50.3817 | 496 | 24.9893
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 28 | 5.8 | 175.8207 | 0.277 | 48.7023 | 496 | 24.1564
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.6 | 28 | 5.6 | 169.7579 | 0.277 | 47.023 | 480 | 22.571
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.7 | 28 | 5.7 | 172.7893 | 0.277 | 47.8626 | 496 | 23.7399
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.5 | 28 | 5.5 | 166.7266 | 0.277 | 46.1833 | 480 | 22.168
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 28 | 5.2 | 157.6324 | 0.277 | 43.6642 | 496 | 21.6574
|  | Tinf for setpoint 28 degrees C | [11 empty] | 308.484
Total Internal Load by People
|  | Month | People | SenL/person | CLF | SensL (W) | Latent/Person | LatentL (W) | Total peo L (W) | AC opn hrs | Total PL (KWh)
|  | Jan | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Feb | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 448 | 188.16
|  | Mar | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Apr | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 | 201.6
|  | May | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Jun | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 | 201.6
|  | Jul | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Aug | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Sep | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 | 201.6
|  | Oct | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Nov | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 | 201.6
|  | Dec | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 | 208.32
|  | Total Internal Load by People | [8 empty] | 2452.8
Total Internal Heat Load of Lights per Year
|  | No. Bulbs | Watt Rating | bf | Fu | CLF | hrs (6hrs/day) | Tihlig(KWh)
|  | 3 | 60 | 1.24 | 0.66 | 0.8 | 2190 | 258.0906
|  | Total Internal Heat Load of Lights per Year | [5 empty] | 258.0906
Total Internal Heat Load-Equipment
|  | TV Rating W | Hrs /day | Total hrs | Tihe (KWh)
|  | 36 | 5 | 1825 | 65.7
|  | Total load Equipment |  |  | 65.7
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 22 | 191.7173 | 267.4925 | 602.7133 | 2452.8 | 258.0906 | 65.7 | 3838.5137
|  | 23 | 163.3349 | 267.4925 | 553.6751 | 2452.8 | 258.0906 | 65.7 | 3761.0931
|  | 24 | 134.9525 | 267.4925 | 504.6369 | 2452.8 | 258.0906 | 65.7 | 3683.6725
|  | 25 | 106.5701 | 267.4925 | 455.5987 | 2452.8 | 258.0906 | 65.7 | 3606.2519
|  | 26 | 78.1877 | 267.4925 | 406.5604 | 2452.8 | 258.0906 | 65.7 | 3528.8313
|  | 27 | 49.8053 | 267.4925 | 357.5222 | 2452.8 | 258.0906 | 65.7 | 3451.4106
|  | 28 | 21.4229 | 267.4925 | 308.484 | 2452.8 | 258.0906 | 65.7 | 3373.99

## All Season Dengue Endemic_IK
Balance Point Temperature, Annual Variable Degree Days, Thermal Load of Living Space and Annual Electricity Consumption Calculations for Chennai- Baseline and Solar Electricity Scenarios
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | AC hrs/24 hrs (fAC) | Conv (24/1000) KWh |  |  | Annual VCDD |  |  |  | Annual VCDD |  |  |  | Annual VCDD |  | All Other Heat Loads | BE+Other Loads | 10%SF |  | EER | Elec. Cons. |  |  | LDRZ Setpoint Adjsuted Preference %
|  | Jan | 22 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9491 | 19 | 229.1 | [22 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Feb | 22 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9376 | 19 | 234.8 | [22 empty] | 22 | 16 | 0.34783
|  | Mar | 22 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9205 | 19 | 264.4 | [22 empty] | 23 | 10 | 0.21739
|  | Apr | 22 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8804 | 19 | 277.6 | [22 empty] | 24 | 20 | 0.43478
|  | May | 22 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.7088 | 18.5 | 308.2 | [23 empty] | 46
|  | Jun | 22 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.6172 | 18.5 | 287.5
|  | July | 22 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.6916 | 18.5 | 299.2
|  | Aug | 22 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8633 | 19 | 281.4
|  | Sep | 22 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.7697 | 19 | 284.7
|  | Oct | 22 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9319 | 19 | 261.9
|  | Nov | 22 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9434 | 19 | 228.1
|  | Dec | 22 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9548 | 19 | 255.3
|  | Annual VCDD | [9 empty] | 3212.2 | 0.66667 | 0.024 | 3.59 | 12.96 | 3212.2 | 2391.2336 | 3.94 | 12.96 | 3212.2 | 2624.3623 | 2.13 | 41.904 | 3212.2 | 4587.3053 | 3696.9557 | 13299.8569 | 1329.9857 | 14629.8426 | 3.1 | 4719 | 22
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 23 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9491 | 20 | 198.1
|  | Feb | 23 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9376 | 20 | 206.8
|  | Mar | 23 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9205 | 20 | 233.4
|  | Apr | 23 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8804 | 20 | 247.6
|  | May | 23 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.7088 | 19.5 | 277.2
|  | Jun | 23 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.6172 | 19.5 | 257.5
|  | July | 23 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.6916 | 19.5 | 268.2
|  | Aug | 23 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8633 | 20 | 250.4
|  | Sep | 23 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.7697 | 20 | 254.7
|  | Oct | 23 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9319 | 20 | 230.9
|  | Nov | 23 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9434 | 20 | 198.1
|  | Dec | 23 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9548 | 20 | 224.3
|  | Annual VCDD | [9 empty] | 2847.2 | 0.66667 | 0.024 | 3.59 | 12.96 | 2847.2 | 2119.5195 | 3.94 | 12.96 | 2847.2 | 2326.1578 | 2.13 | 41.904 | 2847.2 | 4066.0531 | 3619.5351 | 12131.2654 | 1213.1265 | 13344.392 | 3.1 | 4305 | 23
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 24 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9491 | 21 | 167.1
|  | Feb | 24 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9376 | 21 | 178.8
|  | Mar | 24 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9205 | 21 | 202.4
|  | Apr | 24 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8804 | 21 | 217.6
|  | May | 24 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.7088 | 20.5 | 246.2
|  | Jun | 24 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.6172 | 20.5 | 227.5
|  | Jul | 24 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.6916 | 20.5 | 237.2
|  | Aug | 24 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8633 | 21 | 219.4
|  | Sep | 24 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.7697 | 21 | 224.7
|  | Oct | 24 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9319 | 21 | 199.9
|  | Nov | 24 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9434 | 21 | 168.1
|  | Dec | 24 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9548 | 21 | 193.3
|  | Annual VCDD | [9 empty] | 2482.2 | 0.66667 | 0.024 | 3.59 | 12.96 | 2482.2 | 1847.8053 | 3.94 | 12.96 | 2482.2 | 2027.9534 | 2.13 | 41.904 | 2482.2 | 3544.8008 | 3542.1144 | 10962.674 | 1096.2674 | 12058.9414 | 3.1 | 3890 | 24 |  | MDRZ Setpoint Adjsuted Preference %
|  | Avg Energy Consumption of AC Unit for LDRZ | [29 empty] | 4268.5652
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | [22 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Jan | 25 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9491 | 22 | 136.1 | [22 empty] | 25 | 12 | 100
|  | Feb | 25 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9376 | 22 | 151.3
|  | Mar | 25 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9205 | 22 | 171.4
|  | Apr | 25 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8804 | 22 | 187.6
|  | May | 25 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.7088 | 21.5 | 215.2
|  | Jun | 25 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.6172 | 21.5 | 197.5
|  | Jul | 25 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.6916 | 21.5 | 206.2 | [21 empty] | 792.5652
|  | Aug | 25 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8633 | 22 | 188.4
|  | Sep | 25 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.7697 | 22 | 194.7
|  | Oct | 25 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9319 | 22 | 168.9
|  | Nov | 25 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9434 | 22 | 138.1
|  | Dec | 25 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9548 | 22 | 162.3
|  | Annual VCDD | [9 empty] | 2117.7 | 0.66667 | 0.024 | 3.59 | 12.96 | 2117.7 | 1576.4633 | 3.94 | 12.96 | 2117.7 | 1730.1575 | 2.13 | 41.904 | 2117.7 | 3024.2626 | 3464.6938 | 9795.5773 | 979.5577 | 10775.135 | 3.1 | 3476 | 25
|  | Avg Energy Consumption of AC Unit for MDRZ | [29 empty] | 3476
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 26 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9491 | 23 | 105.4
|  | Feb | 26 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9376 | 23 | 124.9
|  | Mar | 26 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9205 | 23 | 140.4
|  | Apr | 26 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8804 | 23 | 157.6
|  | May | 26 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.7088 | 22.5 | 184.2
|  | Jun | 26 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.6172 | 22.5 | 167.5
|  | July | 26 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.6916 | 22.5 | 175.2
|  | Aug | 26 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8633 | 23 | 157.4
|  | Sep | 26 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.7697 | 23 | 164.7
|  | Oct | 26 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9319 | 23 | 137.9
|  | Nov | 26 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9434 | 23 | 108.1
|  | Dec | 26 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9548 | 23 | 131.8
|  | Annual VCDD | [9 empty] | 1755.1 | 0.66667 | 0.024 | 3.59 | 12.96 | 1755.1 | 1306.5358 | 3.94 | 12.96 | 1755.1 | 1433.9139 | 2.13 | 41.904 | 1755.1 | 2506.4378 | 3387.2732 | 8634.1607 | 863.4161 | 9497.5767 | 3.1 | 3064 | 26
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | [22 empty] | HDRZ Setpoint Adjsuted Preference %
|  | Jan | 27 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9491 | 24 | 75.9 | [22 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Feb | 27 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9376 | 24 | 101.2 | [22 empty] | 26 | 10 | 0.5
|  | Mar | 27 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9205 | 24 | 110.1 | [22 empty] | 27 | 8 | 0.4
|  | Apr | 27 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8804 | 24 | 127.6 | [22 empty] | 28 | 2 | 0.1
|  | May | 27 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.7088 | 23.5 | 153.2 | [23 empty] | 20
|  | Jun | 27 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.6172 | 23.5 | 137.5
|  | Jul | 27 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.6916 | 23.5 | 144.2
|  | Aug | 27 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8633 | 24 | 126.4
|  | Sep | 27 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.7697 | 24 | 134.7
|  | Oct | 27 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9319 | 24 | 106.9
|  | Nov | 27 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9434 | 24 | 78.7
|  | Dec | 27 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9548 | 24 | 102.2
|  | Annual VCDD | [9 empty] | 1398.6 | 0.66667 | 0.024 | 3.59 | 12.96 | 1398.6 | 1041.1492 | 3.94 | 12.96 | 1398.6 | 1142.654 | 2.13 | 41.904 | 1398.6 | 1997.3243 | 3309.8526 | 7490.98 | 749.098 | 8240.078 | 3.1 | 2658 | 27
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 28 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9491 | 25 | 53.7
|  | Feb | 28 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9376 | 25 | 80.3
|  | Mar | 28 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9205 | 25 | 84.9
|  | Apr | 28 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8804 | 25 | 99.3
|  | May | 28 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.7088 | 24.5 | 122.5
|  | Jun | 28 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.6172 | 24.5 | 107.6
|  | Jul | 28 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.6916 | 24.5 | 113.4
|  | Aug | 28 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8633 | 25 | 95.8
|  | Sep | 28 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.7697 | 25 | 105.1
|  | Oct | 28 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9319 | 25 | 77.6
|  | Nov | 28 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9434 | 25 | 55.7
|  | Dec | 28 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9548 | 25 | 76.1
|  | Annual VCDD | [9 empty] | 1072 | 0.66667 | 0.024 | 3.59 | 12.96 | 1072 | 798.0208 | 3.94 | 12.96 | 1072 | 875.8223 | 2.13 | 41.904 | 1072 | 1530.9107 | 3232.432 | 6437.1857 | 643.7186 | 7080.9043 | 3.1 | 2284 | 28
|  | Avg Energy Consumption of AC Unit for HDRZ | [29 empty] | 2824 |  | 1444.5652
CLTDgw-avg (°C) for AC Opn hrs. |  | Thermal Conductive Load (TLgw-x) Calculated for Three Climate Zones
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 22°C
AC Opn hrs. | CLTDgw (°C) | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
00.00-01.00 | 1 | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 22 | 3.5 | -1.2 | 4.05 | 3.75 | 1.296 | 496 | 9.7628
01.00-02.00 | 1 | Feb | 32.1 | 6.6 | 3.3 | 28.8 | 1.75 | 22 | 3.5 | -0.6 | 4.65 | 3.75 | 1.296 | 448 | 10.1244
02.00-03.00 | 0 | Mar | 32 | 6 | 3 | 29 | 1.75 | 22 | 3.5 | -0.4 | 4.85 | 3.75 | 1.296 | 496 | 11.6912
03.00-04.00 | -1 | Apr | 32.3 | 5.8 | 2.9 | 29.4 | 1.75 | 22 | 3.5 | 0 | 5.25 | 3.75 | 1.296 | 480 | 12.2472
04.00-05.00 | -1 | May | 31.9 | 4.2 | 2.1 | 29.8 | 1.75 | 22 | 3.5 | 0.4 | 5.65 | 3.75 | 1.296 | 496 | 13.6197
05.00-06.00 | -1 | Jun | 30.8 | 3.5 | 1.75 | 29.05 | 1.75 | 22 | 3.5 | -0.35 | 4.9 | 3.75 | 1.296 | 480 | 11.4307
06.00-07.00 | -1 | Jul | 30.7 | 3.4 | 1.7 | 29 | 1.75 | 22 | 3.5 | -0.4 | 4.85 | 3.75 | 1.296 | 496 | 11.6912
07.00-08.00 | -1 | Aug | 30.5 | 3.3 | 1.65 | 28.85 | 1.75 | 22 | 3.5 | -0.55 | 4.7 | 3.75 | 1.296 | 496 | 11.3296
08.00-09.00 | 0 | Sep | 30.5 | 3.7 | 1.85 | 28.65 | 1.75 | 22 | 3.5 | -0.75 | 4.5 | 3.75 | 1.296 | 480 | 10.4976
17.00-18.00 | 7 | Oct | 30.7 | 4.8 | 2.4 | 28.3 | 1.75 | 22 | 3.5 | -1.1 | 4.15 | 3.75 | 1.296 | 496 | 10.0038
18.00-19.00 | 7 | Nov | 31.1 | 5.7 | 2.85 | 28.25 | 1.75 | 22 | 3.5 | -1.15 | 4.1 | 3.75 | 1.296 | 480 | 9.5645
19.00-20.00 | 6 | Dec | 31.2 | 6 | 3 | 28.2 | 1.75 | 22 | 3.5 | -1.2 | 4.05 | 3.75 | 1.296 | 496 | 9.7628
20.00-21.00 | 4 | TLgw-CHN (KWh) | [12 empty] | 131.7254
21.00-22.00 | 3 | Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 23°C
22.00-23.00 | 2 | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 23 | 2.5 | -1.2 | 3.05 | 3.75 | 1.296 | 496 | 7.3522
23.00-00.00 | 2 | Feb | 32.1 | 6.6 | 3.3 | 28.8 | 1.75 | 23 | 2.5 | -0.6 | 3.65 | 3.75 | 1.296 | 448 | 7.9471
CLTDgw-avg (°C) | 1.75 | Mar | 32 | 6 | 3 | 29 | 1.75 | 23 | 2.5 | -0.4 | 3.85 | 3.75 | 1.296 | 496 | 9.2807
|  | Apr | 32.3 | 5.8 | 2.9 | 29.4 | 1.75 | 23 | 2.5 | 0 | 4.25 | 3.75 | 1.296 | 480 | 9.9144
|  | May | 31.9 | 4.2 | 2.1 | 29.8 | 1.75 | 23 | 2.5 | 0.4 | 4.65 | 3.75 | 1.296 | 496 | 11.2091
|  | Jun | 30.8 | 3.5 | 1.75 | 29.05 | 1.75 | 23 | 2.5 | -0.35 | 3.9 | 3.75 | 1.296 | 480 | 9.0979
|  | Jul | 30.7 | 3.4 | 1.7 | 29 | 1.75 | 23 | 2.5 | -0.4 | 3.85 | 3.75 | 1.296 | 496 | 9.2807
|  | Aug | 30.5 | 3.3 | 1.65 | 28.85 | 1.75 | 23 | 2.5 | -0.55 | 3.7 | 3.75 | 1.296 | 496 | 8.9191
|  | Sep | 30.5 | 3.7 | 1.85 | 28.65 | 1.75 | 23 | 2.5 | -0.75 | 3.5 | 3.75 | 1.296 | 480 | 8.1648
|  | Oct | 30.7 | 4.8 | 2.4 | 28.3 | 1.75 | 23 | 2.5 | -1.1 | 3.15 | 3.75 | 1.296 | 496 | 7.5933
|  | Nov | 31.1 | 5.7 | 2.85 | 28.25 | 1.75 | 23 | 2.5 | -1.15 | 3.1 | 3.75 | 1.296 | 480 | 7.2317
|  | Dec | 31.2 | 6 | 3 | 28.2 | 1.75 | 23 | 2.5 | -1.2 | 3.05 | 3.75 | 1.296 | 496 | 7.3522
|  | TLgw-CHN (KWh) | [12 empty] | 103.343
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 24°C
|  | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 24 | 1.5 | -1.2 | 2.05 | 3.75 | 1.296 | 496 | 4.9416
|  | Feb | 32.1 | 6.6 | 3.3 | 28.8 | 1.75 | 24 | 1.5 | -0.6 | 2.65 | 3.75 | 1.296 | 448 | 5.7698
|  | Mar | 32 | 6 | 3 | 29 | 1.75 | 24 | 1.5 | -0.4 | 2.85 | 3.75 | 1.296 | 496 | 6.8701
|  | Apr | 32.3 | 5.8 | 2.9 | 29.4 | 1.75 | 24 | 1.5 | 0 | 3.25 | 3.75 | 1.296 | 480 | 7.5816
|  | May | 31.9 | 4.2 | 2.1 | 29.8 | 1.75 | 24 | 1.5 | 0.4 | 3.65 | 3.75 | 1.296 | 496 | 8.7985
|  | Jun | 30.8 | 3.5 | 1.75 | 29.05 | 1.75 | 24 | 1.5 | -0.35 | 2.9 | 3.75 | 1.296 | 480 | 6.7651
|  | Jul | 30.7 | 3.4 | 1.7 | 29 | 1.75 | 24 | 1.5 | -0.4 | 2.85 | 3.75 | 1.296 | 496 | 6.8701
|  | Aug | 30.5 | 3.3 | 1.65 | 28.85 | 1.75 | 24 | 1.5 | -0.55 | 2.7 | 3.75 | 1.296 | 496 | 6.5085
|  | Sep | 30.5 | 3.7 | 1.85 | 28.65 | 1.75 | 24 | 1.5 | -0.75 | 2.5 | 3.75 | 1.296 | 480 | 5.832
|  | Oct | 30.7 | 4.8 | 2.4 | 28.3 | 1.75 | 24 | 1.5 | -1.1 | 2.15 | 3.75 | 1.296 | 496 | 5.1827
|  | Nov | 31.1 | 5.7 | 2.85 | 28.25 | 1.75 | 24 | 1.5 | -1.15 | 2.1 | 3.75 | 1.296 | 480 | 4.8989
|  | Dec | 31.2 | 6 | 3 | 28.2 | 1.75 | 24 | 1.5 | -1.2 | 2.05 | 3.75 | 1.296 | 496 | 4.9416
|  | TLgw-AMD (KWh) | [12 empty] | 74.9606
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 25°C
|  | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 25 | 0.5 | -1.2 | 1.05 | 3.75 | 1.296 | 496 | 2.5311
|  | Feb | 32.1 | 6.6 | 3.3 | 28.8 | 1.75 | 25 | 0.5 | -0.6 | 1.65 | 3.75 | 1.296 | 448 | 3.5925
|  | Mar | 32 | 6 | 3 | 29 | 1.75 | 25 | 0.5 | -0.4 | 1.85 | 3.75 | 1.296 | 496 | 4.4595
|  | Apr | 32.3 | 5.8 | 2.9 | 29.4 | 1.75 | 25 | 0.5 | 0 | 2.25 | 3.75 | 1.296 | 480 | 5.2488
|  | May | 31.9 | 4.2 | 2.1 | 29.8 | 1.75 | 25 | 0.5 | 0.4 | 2.65 | 3.75 | 1.296 | 496 | 6.388
|  | Jun | 30.8 | 3.5 | 1.75 | 29.05 | 1.75 | 25 | 0.5 | -0.35 | 1.9 | 3.75 | 1.296 | 480 | 4.4323
|  | Jul | 30.7 | 3.4 | 1.7 | 29 | 1.75 | 25 | 0.5 | -0.4 | 1.85 | 3.75 | 1.296 | 496 | 4.4595
|  | Aug | 30.5 | 3.3 | 1.65 | 28.85 | 1.75 | 25 | 0.5 | -0.55 | 1.7 | 3.75 | 1.296 | 496 | 4.098
|  | Sep | 30.5 | 3.7 | 1.85 | 28.65 | 1.75 | 25 | 0.5 | -0.75 | 1.5 | 3.75 | 1.296 | 480 | 3.4992
|  | Oct | 30.7 | 4.8 | 2.4 | 28.3 | 1.75 | 25 | 0.5 | -1.1 | 1.15 | 3.75 | 1.296 | 496 | 2.7721
|  | Nov | 31.1 | 5.7 | 2.85 | 28.25 | 1.75 | 25 | 0.5 | -1.15 | 1.1 | 3.75 | 1.296 | 480 | 2.5661
|  | Dec | 31.2 | 6 | 3 | 28.2 | 1.75 | 25 | 0.5 | -1.2 | 1.05 | 3.75 | 1.296 | 496 | 2.5311
|  | TLgw-DEL (KWh) | [12 empty] | 46.5782
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 26°C
|  | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 26 | -0.5 | -1.2 | 0.05 | 3.75 | 1.296 | 496 | 0.12053
|  | Feb | 32.1 | 6.6 | 3.3 | 28.8 | 1.75 | 26 | -0.5 | -0.6 | 0.65 | 3.75 | 1.296 | 448 | 1.4152
|  | Mar | 32 | 6 | 3 | 29 | 1.75 | 26 | -0.5 | -0.4 | 0.85 | 3.75 | 1.296 | 496 | 2.049
|  | Apr | 32.3 | 5.8 | 2.9 | 29.4 | 1.75 | 26 | -0.5 | 0 | 1.25 | 3.75 | 1.296 | 480 | 2.916
|  | May | 31.9 | 4.2 | 2.1 | 29.8 | 1.75 | 26 | -0.5 | 0.4 | 1.65 | 3.75 | 1.296 | 496 | 3.9774
|  | Jun | 30.8 | 3.5 | 1.75 | 29.05 | 1.75 | 26 | -0.5 | -0.35 | 0.9 | 3.75 | 1.296 | 480 | 2.0995
|  | Jul | 30.7 | 3.4 | 1.7 | 29 | 1.75 | 26 | -0.5 | -0.4 | 0.85 | 3.75 | 1.296 | 496 | 2.049
|  | Aug | 30.5 | 3.3 | 1.65 | 28.85 | 1.75 | 26 | -0.5 | -0.55 | 0.7 | 3.75 | 1.296 | 496 | 1.6874
|  | Sep | 30.5 | 3.7 | 1.85 | 28.65 | 1.75 | 26 | -0.5 | -0.75 | 0.5 | 3.75 | 1.296 | 480 | 1.1664
|  | Oct | 30.7 | 4.8 | 2.4 | 28.3 | 1.75 | 26 | -0.5 | -1.1 | 0.15 | 3.75 | 1.296 | 496 | 0.36158
|  | Nov | 31.1 | 5.7 | 2.85 | 28.25 | 1.75 | 26 | -0.5 | -1.15 | 0.1 | 3.75 | 1.296 | 480 | 0.23328
|  | Dec | 31.2 | 6 | 3 | 28.2 | 1.75 | 26 | -0.5 | -1.2 | 0.05 | 3.75 | 1.296 | 496 | 0.12053
|  | TLgw-DEL (KWh) | [12 empty] | 18.1958
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 27°C
|  | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 27 | -1.5 | -1.2 | -0.95 | 3.75 | 1.296 | 496 | -2.29
|  | Feb | 32.1 | 6.6 | 3.3 | 28.8 | 1.75 | 27 | -1.5 | -0.6 | -0.35 | 3.75 | 1.296 | 448 | -0.76205
|  | Mar | 32 | 6 | 3 | 29 | 1.75 | 27 | -1.5 | -0.4 | -0.15 | 3.75 | 1.296 | 496 | -0.36158
|  | Apr | 32.3 | 5.8 | 2.9 | 29.4 | 1.75 | 27 | -1.5 | 0 | 0.25 | 3.75 | 1.296 | 480 | 0.5832
|  | May | 31.9 | 4.2 | 2.1 | 29.8 | 1.75 | 27 | -1.5 | 0.4 | 0.65 | 3.75 | 1.296 | 496 | 1.5669
|  | Jun | 30.8 | 3.5 | 1.75 | 29.05 | 1.75 | 27 | -1.5 | -0.35 | -0.1 | 3.75 | 1.296 | 480 | -0.23328
|  | Jul | 30.7 | 3.4 | 1.7 | 29 | 1.75 | 27 | -1.5 | -0.4 | -0.15 | 3.75 | 1.296 | 496 | -0.36158
|  | Aug | 30.5 | 3.3 | 1.65 | 28.85 | 1.75 | 27 | -1.5 | -0.55 | -0.3 | 3.75 | 1.296 | 496 | -0.72317
|  | Sep | 30.5 | 3.7 | 1.85 | 28.65 | 1.75 | 27 | -1.5 | -0.75 | -0.5 | 3.75 | 1.296 | 480 | -1.1664
|  | Oct | 30.7 | 4.8 | 2.4 | 28.3 | 1.75 | 27 | -1.5 | -1.1 | -0.85 | 3.75 | 1.296 | 496 | -2.049
|  | Nov | 31.1 | 5.7 | 2.85 | 28.25 | 1.75 | 27 | -1.5 | -1.15 | -0.9 | 3.75 | 1.296 | 480 | -2.0995
|  | Dec | 31.2 | 6 | 3 | 28.2 | 1.75 | 27 | -1.5 | -1.2 | -0.95 | 3.75 | 1.296 | 496 | -2.29
|  | TLgw-DEL (KWh) | [12 empty] | -10.1866
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 28°C
|  | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 28 | -2.5 | -1.2 | -1.95 | 3.75 | 1.296 | 496 | -4.7006
|  | Feb | 32.1 | 6.6 | 3.3 | 28.8 | 1.75 | 28 | -2.5 | -0.6 | -1.35 | 3.75 | 1.296 | 448 | -2.9393
|  | Mar | 32 | 6 | 3 | 29 | 1.75 | 28 | -2.5 | -0.4 | -1.15 | 3.75 | 1.296 | 496 | -2.7721
|  | Apr | 32.3 | 5.8 | 2.9 | 29.4 | 1.75 | 28 | -2.5 | 0 | -0.75 | 3.75 | 1.296 | 480 | -1.7496
|  | May | 31.9 | 4.2 | 2.1 | 29.8 | 1.75 | 28 | -2.5 | 0.4 | -0.35 | 3.75 | 1.296 | 496 | -0.8437
|  | Jun | 30.8 | 3.5 | 1.75 | 29.05 | 1.75 | 28 | -2.5 | -0.35 | -1.1 | 3.75 | 1.296 | 480 | -2.5661
|  | Jul | 30.7 | 3.4 | 1.7 | 29 | 1.75 | 28 | -2.5 | -0.4 | -1.15 | 3.75 | 1.296 | 496 | -2.7721
|  | Aug | 30.5 | 3.3 | 1.65 | 28.85 | 1.75 | 28 | -2.5 | -0.55 | -1.3 | 3.75 | 1.296 | 496 | -3.1337
|  | Sep | 30.5 | 3.7 | 1.85 | 28.65 | 1.75 | 28 | -2.5 | -0.75 | -1.5 | 3.75 | 1.296 | 480 | -3.4992
|  | Oct | 30.7 | 4.8 | 2.4 | 28.3 | 1.75 | 28 | -2.5 | -1.1 | -1.85 | 3.75 | 1.296 | 496 | -4.4595
|  | Nov | 31.1 | 5.7 | 2.85 | 28.25 | 1.75 | 28 | -2.5 | -1.15 | -1.9 | 3.75 | 1.296 | 480 | -4.4323
|  | Dec | 31.2 | 6 | 3 | 28.2 | 1.75 | 28 | -2.5 | -1.2 | -1.95 | 3.75 | 1.296 | 496 | -4.7006
|  | TLgw-DEL (KWh) | [12 empty] | -38.569
Annual Radiation Thermal Load Through Glass Window
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jan | 0.55 | 0.51 | 100.94 | 1.296 | 496 | 18.2005
|  | Feb | 0.55 | 0.51 | 107.25 | 1.296 | 448 | 17.4668
|  | Mar | 0.55 | 0.51 | 116.71 | 1.296 | 496 | 21.044
|  | Apr | 0.55 | 0.51 | 138.8 | 1.296 | 480 | 24.2197
|  | May | 0.55 | 0.51 | 233.43 | 1.296 | 496 | 42.0897
|  | Jun | 0.55 | 0.51 | 283.91 | 1.296 | 480 | 49.5404
|  | Jul | 0.55 | 0.51 | 242.9 | 1.296 | 496 | 43.7973
|  | Aug | 0.55 | 0.51 | 148.26 | 1.296 | 496 | 26.7327
|  | Sep | 0.55 | 0.51 | 199.87 | 1.296 | 480 | 34.876
|  | Oct | 0.55 | 0.51 | 110.41 | 1.296 | 496 | 19.908
|  | Nov | 0.55 | 0.51 | 104.1 | 1.296 | 480 | 18.1648
|  | Dec | 0.55 | 0.51 | 97.79 | 1.296 | 496 | 17.6325
|  | TLrad | [5 empty] | 333.6724
Inflitration Load for Different Setpoint Temperatures
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) |  | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 22 | 9.6 | 291.0136 |  | 0.277 | 80.6108 | 496 | 39.9829
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 22 | 10.1 | 306.1706 |  | 0.277 | 84.8093 | 448 | 37.9945
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32 | 22 | 10 | 303.1392 |  | 0.277 | 83.9696 | 496 | 41.6489
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.3 | 22 | 10.3 | 312.2334 |  | 0.277 | 86.4886 | 480 | 41.5145
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 22 | 9.9 | 300.1078 |  | 0.277 | 83.1299 | 496 | 41.2324
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 22 | 8.8 | 266.7625 |  | 0.277 | 73.8932 | 480 | 35.4687
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 22 | 8.7 | 263.7311 |  | 0.277 | 73.0535 | 496 | 36.2345
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 22 | 8.5 | 257.6683 |  | 0.277 | 71.3741 | 496 | 35.4016
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 22 | 8.5 | 257.6683 |  | 0.277 | 71.3741 | 480 | 34.2596
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 22 | 8.7 | 263.7311 |  | 0.277 | 73.0535 | 496 | 36.2345
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.1 | 22 | 9.1 | 275.8567 |  | 0.277 | 76.4123 | 480 | 36.6779
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 22 | 9.2 | 278.8881 |  | 0.277 | 77.252 | 496 | 38.317
|  | Tinf for setpoint 22 degrees C | [12 empty] | 454.9672
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 23 | 8.6 | 260.6997 |  | 0.277 | 72.2138 | 496 | 35.8181
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 23 | 9.1 | 275.8567 |  | 0.277 | 76.4123 | 448 | 34.2327
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32 | 23 | 9 | 272.8253 |  | 0.277 | 75.5726 | 496 | 37.484
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.3 | 23 | 9.3 | 281.9195 |  | 0.277 | 78.0917 | 480 | 37.484
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 23 | 8.9 | 269.7939 |  | 0.277 | 74.7329 | 496 | 37.0675
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 23 | 7.8 | 236.4486 |  | 0.277 | 65.4963 | 480 | 31.4382
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 23 | 7.7 | 233.4172 |  | 0.277 | 64.6566 | 496 | 32.0697
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 23 | 7.5 | 227.3544 |  | 0.277 | 62.9772 | 496 | 31.2367
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 23 | 7.5 | 227.3544 |  | 0.277 | 62.9772 | 480 | 30.229
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 23 | 7.7 | 233.4172 |  | 0.277 | 64.6566 | 496 | 32.0697
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.1 | 23 | 8.1 | 245.5427 |  | 0.277 | 68.0153 | 480 | 32.6474
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 23 | 8.2 | 248.5741 |  | 0.277 | 68.855 | 496 | 34.1521
|  | Tinf for setpoint 23 degrees C | [12 empty] | 405.929
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 24 | 7.6 | 230.3858 |  | 0.277 | 63.8169 | 496 | 31.6532
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 24 | 8.1 | 245.5427 |  | 0.277 | 68.0153 | 448 | 30.4709
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32 | 24 | 8 | 242.5114 |  | 0.277 | 67.1756 | 496 | 33.3191
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.3 | 24 | 8.3 | 251.6055 |  | 0.277 | 69.6947 | 480 | 33.4535
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 24 | 7.9 | 239.48 |  | 0.277 | 66.336 | 496 | 32.9026
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 24 | 6.8 | 206.1347 |  | 0.277 | 57.0993 | 480 | 27.4077
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 24 | 6.7 | 203.1033 |  | 0.277 | 56.2596 | 496 | 27.9048
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 24 | 6.5 | 197.0405 |  | 0.277 | 54.5802 | 496 | 27.0718
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 24 | 6.5 | 197.0405 |  | 0.277 | 54.5802 | 480 | 26.1985
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 24 | 6.7 | 203.1033 |  | 0.277 | 56.2596 | 496 | 27.9048
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.1 | 24 | 7.1 | 215.2288 |  | 0.277 | 59.6184 | 480 | 28.6168
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 24 | 7.2 | 218.2602 |  | 0.277 | 60.4581 | 496 | 29.9872
|  | Tinf for setpoint 24 degrees C | [12 empty] | 356.8908
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 25 | 6.6 | 200.0719 |  | 0.277 | 55.4199 | 496 | 27.4883
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 25 | 7.1 | 215.2288 |  | 0.277 | 59.6184 | 448 | 26.709
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32 | 25 | 7 | 212.1974 |  | 0.277 | 58.7787 | 496 | 29.1542
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.3 | 25 | 7.3 | 221.2916 |  | 0.277 | 61.2978 | 480 | 29.4229
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 25 | 6.9 | 209.166 |  | 0.277 | 57.939 | 496 | 28.7377
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 25 | 5.8 | 175.8207 |  | 0.277 | 48.7023 | 480 | 23.3771
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 25 | 5.7 | 172.7893 |  | 0.277 | 47.8626 | 496 | 23.7399
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 25 | 5.5 | 166.7266 |  | 0.277 | 46.1833 | 496 | 22.9069
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 25 | 5.5 | 166.7266 |  | 0.277 | 46.1833 | 480 | 22.168
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 25 | 5.7 | 172.7893 |  | 0.277 | 47.8626 | 496 | 23.7399
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.1 | 25 | 6.1 | 184.9149 |  | 0.277 | 51.2214 | 480 | 24.5863
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 25 | 6.2 | 187.9463 |  | 0.277 | 52.0611 | 496 | 25.8223
|  | Tinf for setpoint 25 degrees C | [12 empty] | 307.8525
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 26 | 5.6 | 169.7579 |  | 0.277 | 47.023 | 496 | 23.3234
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 26 | 6.1 | 184.9149 |  | 0.277 | 51.2214 | 448 | 22.9472
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32 | 26 | 6 | 181.8835 |  | 0.277 | 50.3817 | 496 | 24.9893
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.3 | 26 | 6.3 | 190.9777 |  | 0.277 | 52.9008 | 480 | 25.3924
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 26 | 5.9 | 178.8521 |  | 0.277 | 49.542 | 496 | 24.5729
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 26 | 4.8 | 145.5068 |  | 0.277 | 40.3054 | 480 | 19.3466
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 26 | 4.7 | 142.4754 |  | 0.277 | 39.4657 | 496 | 19.575
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 26 | 4.5 | 136.4126 |  | 0.277 | 37.7863 | 496 | 18.742
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 26 | 4.5 | 136.4126 |  | 0.277 | 37.7863 | 480 | 18.1374
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 26 | 4.7 | 142.4754 |  | 0.277 | 39.4657 | 496 | 19.575
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.1 | 26 | 5.1 | 154.601 |  | 0.277 | 42.8245 | 480 | 20.5557
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 26 | 5.2 | 157.6324 |  | 0.277 | 43.6642 | 496 | 21.6574
|  | Tinf for setpoint 26 degrees C | [12 empty] | 258.8143
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 27 | 4.6 | 139.444 |  | 0.277 | 38.626 | 496 | 19.1585
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 27 | 5.1 | 154.601 |  | 0.277 | 42.8245 | 448 | 19.1854
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32 | 27 | 5 | 151.5696 |  | 0.277 | 41.9848 | 496 | 20.8245
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.3 | 27 | 5.3 | 160.6638 |  | 0.277 | 44.5039 | 480 | 21.3619
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 27 | 4.9 | 148.5382 |  | 0.277 | 41.1451 | 496 | 20.408
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 27 | 3.8 | 115.1929 |  | 0.277 | 31.9084 | 480 | 15.316
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 27 | 3.7 | 112.1615 |  | 0.277 | 31.0687 | 496 | 15.4101
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 27 | 3.5 | 106.0987 |  | 0.277 | 29.3893 | 496 | 14.5771
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 27 | 3.5 | 106.0987 |  | 0.277 | 29.3893 | 480 | 14.1069
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 27 | 3.7 | 112.1615 |  | 0.277 | 31.0687 | 496 | 15.4101
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.1 | 27 | 4.1 | 124.2871 |  | 0.277 | 34.4275 | 480 | 16.5252
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 27 | 4.2 | 127.3185 |  | 0.277 | 35.2672 | 496 | 17.4925
|  | Tinf for setpoint 27 degrees C | [12 empty] | 209.7761
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 28 | 3.6 | 109.1301 |  | 0.277 | 30.229 | 496 | 14.9936
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 28 | 4.1 | 124.2871 |  | 0.277 | 34.4275 | 448 | 15.4235
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32 | 28 | 4 | 121.2557 |  | 0.277 | 33.5878 | 496 | 16.6596
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.3 | 28 | 4.3 | 130.3499 |  | 0.277 | 36.1069 | 480 | 17.3313
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 28 | 3.9 | 118.2243 |  | 0.277 | 32.7481 | 496 | 16.2431
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 30.8 | 28 | 2.8 | 84.879 |  | 0.277 | 23.5115 | 480 | 11.2855
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 28 | 2.7 | 81.8476 |  | 0.277 | 22.6718 | 496 | 11.2452
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 28 | 2.5 | 75.7848 |  | 0.277 | 20.9924 | 496 | 10.4122
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 30.5 | 28 | 2.5 | 75.7848 |  | 0.277 | 20.9924 | 480 | 10.0763
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 30.7 | 28 | 2.7 | 81.8476 |  | 0.277 | 22.6718 | 496 | 11.2452
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.1 | 28 | 3.1 | 93.9732 |  | 0.277 | 26.0306 | 480 | 12.4947
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 28 | 3.2 | 97.0045 |  | 0.277 | 26.8703 | 496 | 13.3276
|  | Tinf for setpoint 28 degrees C | [12 empty] | 160.7379
Total Internal Load by People
|  | Month | People | SenL/person | CLF | SensL (W) | Latent/Person | LatentL (W) | Total peo L (W) | AC opn hrs |  | Total PL (KWh)
|  | Jan | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Feb | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 448 |  | 188.16
|  | Mar | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Apr | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | May | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Jun | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Jul | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Aug | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Sep | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Oct | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Nov | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Dec | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Total Internal Load by People | [9 empty] | 2452.8
Total Internal Heat Load of Lights per Year
|  | No. Bulbs | Watt Rating | bf | Fu | CLF | hrs (6hrs/day) | Tihlig(KWh)
|  | 3 | 60 | 1.24 | 0.66 | 0.8 | 2190 | 258.0906
|  | Total Internal Heat Load of Lights per Year | [5 empty] | 258.0906
Total Internal Heat Load-Equipment
|  | TV Rating W | Hrs /day | Total hrs | Tihe (KWh)
|  | 36 | 5 | 1825 | 65.7
|  | Total load Equipment |  |  | 65.7
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 22 | 131.7254 | 333.6724 | 454.9672 | 2452.8 | 258.0906 | 65.7 | 3696.9557
|  | 23 | 103.343 | 333.6724 | 405.929 | 2452.8 | 258.0906 | 65.7 | 3619.5351
|  | 24 | 74.9606 | 333.6724 | 356.8908 | 2452.8 | 258.0906 | 65.7 | 3542.1144
|  | 25 | 46.5782 | 333.6724 | 307.8525 | 2452.8 | 258.0906 | 65.7 | 3464.6938
|  | 26 | 18.1958 | 333.6724 | 258.8143 | 2452.8 | 258.0906 | 65.7 | 3387.2732
|  | 27 | -10.1866 | 333.6724 | 209.7761 | 2452.8 | 258.0906 | 65.7 | 3309.8526
|  | 28 | -38.569 | 333.6724 | 160.7379 | 2452.8 | 258.0906 | 65.7 | 3232.432

## All Season Dengue Endemic_BD
Balance Point Temperature, Annual Variable Degree Days, Thermal Load of Living Space and Annual Electricity Consumption Calculations for Chennai- Baseline and Solar Electricity Scenarios
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | AC hrs/24 hrs (fAC) | Conv (24/1000) KWh |  |  | Annual VCDD |  |  |  | Annual VCDD |  |  |  | Annual VCDD |  | All Other Heat Loads | BE+Other Loads | 10%SF |  | EER | Elec. Cons.
|  | Jan | 22 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9777 | 19 | 56.8 | [21 empty] | LDRZ Setpoint Adjsuted Preference %
|  | Feb | 22 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9605 | 19 | 125 | [21 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Mar | 22 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9376 | 19 | 265.8 | [21 empty] | 22 | 16 | 0.34783
|  | Apr | 22 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9205 | 19 | 293 | [21 empty] | 23 | 10 | 0.21739
|  | May | 22 | 49.3089 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8862 | 19 | 338 | [21 empty] | 24 | 20 | 0.43478
|  | Jun | 22 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8175 | 19 | 322.9 | [22 empty] | 46
|  | July | 22 | 51.6028 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8747 | 19 | 330.7
|  | Aug | 22 | 43.5761 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9148 | 19 | 295.2
|  | Sep | 22 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9319 | 19 | 316.2
|  | Oct | 22 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9548 | 19 | 282.5
|  | Nov | 22 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9777 | 19 | 190.5
|  | Dec | 22 | 29.8129 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9834 | 19 | 74
|  | Annual VCDD | [9 empty] | 2890.6 | 0.66667 | 0.024 | 3.59 | 12.96 | 2890.6 | 2151.8274 | 3.94 | 12.96 | 2890.6 | 2361.6156 | 2.13 | 41.904 | 2890.6 | 4128.0321 | 3693.2854 | 12334.7605 | 1233.476 | 13568.2365 | 3.1 | 4377 | 22
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 23 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9777 | 20 | 42.6
|  | Feb | 23 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9605 | 20 | 101.4
|  | Mar | 23 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9376 | 20 | 234.9
|  | Apr | 23 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9205 | 20 | 263
|  | May | 23 | 49.3089 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8862 | 20 | 307
|  | Jun | 23 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8175 | 20 | 292.9
|  | July | 23 | 51.6028 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8747 | 20 | 299.7
|  | Aug | 23 | 43.5761 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9148 | 20 | 264.2
|  | Sep | 23 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9319 | 20 | 286.2
|  | Oct | 23 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9548 | 20 | 251.5
|  | Nov | 23 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9777 | 20 | 161.3
|  | Dec | 23 | 29.8129 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9834 | 20 | 56.8
|  | Annual VCDD | [9 empty] | 2561.5 | 0.66667 | 0.024 | 3.59 | 12.96 | 2561.5 | 1906.838 | 3.94 | 12.96 | 2561.5 | 2092.7414 | 2.13 | 41.904 | 2561.5 | 3658.0482 | 3615.8648 | 11273.4924 | 1127.3492 | 12400.8417 | 3.1 | 4000 | 23
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 24 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9777 | 21 | 30.3
|  | Feb | 24 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9605 | 21 | 80.1
|  | Mar | 24 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9376 | 21 | 204.6
|  | Apr | 24 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9205 | 21 | 233
|  | May | 24 | 49.3089 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8862 | 21 | 276
|  | Jun | 24 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8175 | 21 | 262.9
|  | Jul | 24 | 51.6028 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8747 | 21 | 268.7
|  | Aug | 24 | 43.5761 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9148 | 21 | 233.2
|  | Sep | 24 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9319 | 21 | 256.2
|  | Oct | 24 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9548 | 21 | 220.5
|  | Nov | 24 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9777 | 21 | 133.8
|  | Dec | 24 | 29.8129 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9834 | 21 | 42.3
|  | Annual VCDD | [9 empty] | 2241.6 | 0.66667 | 0.024 | 3.59 | 12.96 | 2241.6 | 1668.6973 | 3.94 | 12.96 | 2241.6 | 1831.3836 | 2.13 | 41.904 | 2241.6 | 3201.2028 | 3538.4442 | 10239.7278 | 1023.9728 | 11263.7006 | 3.1 | 3633 | 24
|  | Avg Energy Consumption of AC Unit for LDRZ | [29 empty] | 3971.5652
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | [21 empty] | MDRZ Setpoint Adjsuted Preference %
|  | Jan | 25 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9777 | 22 | 21.2 | [21 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Feb | 25 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9605 | 22 | 61.5 | [21 empty] | 25 | 12 | 100
|  | Mar | 25 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9376 | 22 | 174.6
|  | Apr | 25 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9205 | 22 | 203
|  | May | 25 | 49.3089 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8862 | 22 | 245
|  | Jun | 25 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8175 | 22 | 232.9
|  | Jul | 25 | 51.6028 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8747 | 22 | 237.7
|  | Aug | 25 | 43.5761 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9148 | 22 | 202.2
|  | Sep | 25 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9319 | 22 | 226.2
|  | Oct | 25 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9548 | 22 | 189.5
|  | Nov | 25 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9777 | 22 | 108.4
|  | Dec | 25 | 29.8129 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9834 | 22 | 30
|  | Annual VCDD | [9 empty] | 1932.2 | 0.66667 | 0.024 | 3.59 | 12.96 | 1932.2 | 1438.373 | 3.94 | 12.96 | 1932.2 | 1578.6043 | 2.13 | 41.904 | 1932.2 | 2759.3523 | 3461.0236 | 9237.3531 | 923.7353 | 10161.0884 | 3.1 | 3278
|  | Avg Energy Consumption of AC Unit for MDRZ | [29 empty] | 3278 | 25
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 26 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9777 | 23 | 13.5
|  | Feb | 26 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9605 | 23 | 46.4
|  | Mar | 26 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9376 | 23 | 146.1
|  | Apr | 26 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9205 | 23 | 173.4
|  | May | 26 | 49.3089 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8862 | 23 | 214.1
|  | Jun | 26 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8175 | 23 | 202.9
|  | July | 26 | 51.6028 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8747 | 23 | 206.7
|  | Aug | 26 | 43.5761 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9148 | 23 | 171.2
|  | Sep | 26 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9319 | 23 | 196.2
|  | Oct | 26 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9548 | 23 | 158.5
|  | Nov | 26 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9777 | 23 | 85.3
|  | Dec | 26 | 29.8129 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9834 | 23 | 20.3
|  | Annual VCDD | [9 empty] | 1634.6 | 0.66667 | 0.024 | 3.59 | 12.96 | 1634.6 | 1216.8329 | 3.94 | 12.96 | 1634.6 | 1335.4656 | 2.13 | 41.904 | 1634.6 | 2334.3532 | 3383.6029 | 8270.2546 | 827.0255 | 9097.28 | 3.1 | 2935 | 26
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 27 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9777 | 24 | 7.9 | [21 empty] | HDRZ Setpoint Adjsuted Preference %
|  | Feb | 27 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9605 | 24 | 33.3 | [21 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Mar | 27 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9376 | 24 | 119.6 | [21 empty] | 26 | 10 | 0.5
|  | Apr | 27 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9205 | 24 | 144.7 | [21 empty] | 27 | 8 | 0.4
|  | May | 27 | 49.3089 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8862 | 24 | 184 | [21 empty] | 28 | 2 | 0.1
|  | Jun | 27 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8175 | 24 | 172.9 | [22 empty] | 20
|  | Jul | 27 | 51.6028 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8747 | 24 | 175.7
|  | Aug | 27 | 43.5761 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9148 | 24 | 140.2
|  | Sep | 27 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9319 | 24 | 166.2
|  | Oct | 27 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9548 | 24 | 127.7
|  | Nov | 27 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9777 | 24 | 65
|  | Dec | 27 | 29.8129 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9834 | 24 | 12.3
|  | Annual VCDD | [9 empty] | 1349.5 | 0.66667 | 0.024 | 3.59 | 12.96 | 1349.5 | 1004.598 | 3.94 | 12.96 | 1349.5 | 1102.5393 | 2.13 | 41.904 | 1349.5 | 1927.2052 | 3306.1823 | 7340.5249 | 734.0525 | 8074.5774 | 3.1 | 2605 | 27
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 28 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9777 | 25 | 3.7
|  | Feb | 28 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9605 | 25 | 22.5
|  | Mar | 28 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9376 | 25 | 95.2
|  | Apr | 28 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9205 | 25 | 117.6
|  | May | 28 | 49.3089 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8862 | 25 | 154.4
|  | Jun | 28 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8175 | 25 | 142.9
|  | Jul | 28 | 51.6028 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8747 | 25 | 144.7
|  | Aug | 28 | 43.5761 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9148 | 25 | 109.2
|  | Sep | 28 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9319 | 25 | 136.3
|  | Oct | 28 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9548 | 25 | 97.3
|  | Nov | 28 | 30.9617 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9777 | 25 | 47.2
|  | Dec | 28 | 29.8129 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9834 | 25 | 6.6
|  | Annual VCDD | [9 empty] | 1077.6 | 0.66667 | 0.024 | 3.59 | 12.96 | 1077.6 | 802.1896 | 3.94 | 12.96 | 1077.6 | 880.3975 | 2.13 | 41.904 | 1077.6 | 1538.908 | 3228.7617 | 6450.2567 | 645.0257 | 7095.2824 | 3.1 | 2289 | 28
|  | Avg Energy Consumption of AC Unit for HDRZ | [29 empty] | 2738
CLTDgw-avg (°C) for AC Opn hrs. |  | Thermal Conductive Load (TLgw-x) Calculated for Three Climate Zones
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 22°C
AC Opn hrs. | CLTDgw (°C) | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
00.00-01.00 | 1 | Jan | 26.9 | 10.2 | 5.1 | 21.8 | 1.75 | 22 | 3.5 | -7.6 | -2.35 | 3.75 | 1.296 | 496 | -5.6648
01.00-02.00 | 1 | Feb | 31 | 10.6 | 5.3 | 25.7 | 1.75 | 22 | 3.5 | -3.7 | 1.55 | 3.75 | 1.296 | 448 | 3.3748
02.00-03.00 | 0 | Mar | 34.6 | 10.2 | 5.1 | 29.5 | 1.75 | 22 | 3.5 | 0.1 | 5.35 | 3.75 | 1.296 | 496 | 12.8965
03.00-04.00 | -1 | Apr | 36.8 | 9 | 4.5 | 32.3 | 1.75 | 22 | 3.5 | 2.9 | 8.15 | 3.75 | 1.296 | 480 | 19.0123
04.00-05.00 | -1 | May | 35.9 | 7.7 | 3.85 | 32.05 | 1.75 | 22 | 3.5 | 2.65 | 7.9 | 3.75 | 1.296 | 496 | 19.0434
05.00-06.00 | -1 | Jun | 35.1 | 5.7 | 2.85 | 32.25 | 1.75 | 22 | 3.5 | 2.85 | 8.1 | 3.75 | 1.296 | 480 | 18.8957
06.00-07.00 | -1 | Jul | 34 | 4.8 | 2.4 | 31.6 | 1.75 | 22 | 3.5 | 2.2 | 7.45 | 3.75 | 1.296 | 496 | 17.9587
07.00-08.00 | -1 | Aug | 33.9 | 4.9 | 2.45 | 31.45 | 1.75 | 22 | 3.5 | 2.05 | 7.3 | 3.75 | 1.296 | 496 | 17.5971
08.00-09.00 | 0 | Sep | 34.1 | 5.3 | 2.65 | 31.45 | 1.75 | 22 | 3.5 | 2.05 | 7.3 | 3.75 | 1.296 | 480 | 17.0294
17.00-18.00 | 7 | Oct | 33.8 | 6.4 | 3.2 | 30.6 | 1.75 | 22 | 3.5 | 1.2 | 6.45 | 3.75 | 1.296 | 496 | 15.5481
18.00-19.00 | 7 | Nov | 31.2 | 8.1 | 4.05 | 27.15 | 1.75 | 22 | 3.5 | -2.25 | 3 | 3.75 | 1.296 | 480 | 6.9984
19.00-20.00 | 6 | Dec | 28 | 9 | 4.5 | 23.5 | 1.75 | 22 | 3.5 | -5.9 | -0.65 | 3.75 | 1.296 | 496 | -1.5669
20.00-21.00 | 4 | TLgw-CHN (KWh) | [12 empty] | 141.1227
21.00-22.00 | 3 | Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 23°C
22.00-23.00 | 2 | Jan | 26.9 | 10.2 | 5.1 | 21.8 | 1.75 | 23 | 2.5 | -7.6 | -3.35 | 3.75 | 1.296 | 496 | -8.0754
23.00-00.00 | 2 | Feb | 31 | 10.6 | 5.3 | 25.7 | 1.75 | 23 | 2.5 | -3.7 | 0.55 | 3.75 | 1.296 | 448 | 1.1975
CLTDgw-avg (°C) | 1.75 | Mar | 34.6 | 10.2 | 5.1 | 29.5 | 1.75 | 23 | 2.5 | 0.1 | 4.35 | 3.75 | 1.296 | 496 | 10.4859
|  | Apr | 36.8 | 9 | 4.5 | 32.3 | 1.75 | 23 | 2.5 | 2.9 | 7.15 | 3.75 | 1.296 | 480 | 16.6795
|  | May | 35.9 | 7.7 | 3.85 | 32.05 | 1.75 | 23 | 2.5 | 2.65 | 6.9 | 3.75 | 1.296 | 496 | 16.6329
|  | Jun | 35.1 | 5.7 | 2.85 | 32.25 | 1.75 | 23 | 2.5 | 2.85 | 7.1 | 3.75 | 1.296 | 480 | 16.5629
|  | Jul | 34 | 4.8 | 2.4 | 31.6 | 1.75 | 23 | 2.5 | 2.2 | 6.45 | 3.75 | 1.296 | 496 | 15.5481
|  | Aug | 33.9 | 4.9 | 2.45 | 31.45 | 1.75 | 23 | 2.5 | 2.05 | 6.3 | 3.75 | 1.296 | 496 | 15.1865
|  | Sep | 34.1 | 5.3 | 2.65 | 31.45 | 1.75 | 23 | 2.5 | 2.05 | 6.3 | 3.75 | 1.296 | 480 | 14.6966
|  | Oct | 33.8 | 6.4 | 3.2 | 30.6 | 1.75 | 23 | 2.5 | 1.2 | 5.45 | 3.75 | 1.296 | 496 | 13.1376
|  | Nov | 31.2 | 8.1 | 4.05 | 27.15 | 1.75 | 23 | 2.5 | -2.25 | 2 | 3.75 | 1.296 | 480 | 4.6656
|  | Dec | 28 | 9 | 4.5 | 23.5 | 1.75 | 23 | 2.5 | -5.9 | -1.65 | 3.75 | 1.296 | 496 | -3.9774
|  | TLgw-CHN (KWh) | [12 empty] | 112.7403
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 24°C
|  | Jan | 26.9 | 10.2 | 5.1 | 21.8 | 1.75 | 24 | 1.5 | -7.6 | -4.35 | 3.75 | 1.296 | 496 | -10.4859
|  | Feb | 31 | 10.6 | 5.3 | 25.7 | 1.75 | 24 | 1.5 | -3.7 | -0.45 | 3.75 | 1.296 | 448 | -0.97978
|  | Mar | 34.6 | 10.2 | 5.1 | 29.5 | 1.75 | 24 | 1.5 | 0.1 | 3.35 | 3.75 | 1.296 | 496 | 8.0754
|  | Apr | 36.8 | 9 | 4.5 | 32.3 | 1.75 | 24 | 1.5 | 2.9 | 6.15 | 3.75 | 1.296 | 480 | 14.3467
|  | May | 35.9 | 7.7 | 3.85 | 32.05 | 1.75 | 24 | 1.5 | 2.65 | 5.9 | 3.75 | 1.296 | 496 | 14.2223
|  | Jun | 35.1 | 5.7 | 2.85 | 32.25 | 1.75 | 24 | 1.5 | 2.85 | 6.1 | 3.75 | 1.296 | 480 | 14.2301
|  | Jul | 34 | 4.8 | 2.4 | 31.6 | 1.75 | 24 | 1.5 | 2.2 | 5.45 | 3.75 | 1.296 | 496 | 13.1376
|  | Aug | 33.9 | 4.9 | 2.45 | 31.45 | 1.75 | 24 | 1.5 | 2.05 | 5.3 | 3.75 | 1.296 | 496 | 12.776
|  | Sep | 34.1 | 5.3 | 2.65 | 31.45 | 1.75 | 24 | 1.5 | 2.05 | 5.3 | 3.75 | 1.296 | 480 | 12.3638
|  | Oct | 33.8 | 6.4 | 3.2 | 30.6 | 1.75 | 24 | 1.5 | 1.2 | 4.45 | 3.75 | 1.296 | 496 | 10.727
|  | Nov | 31.2 | 8.1 | 4.05 | 27.15 | 1.75 | 24 | 1.5 | -2.25 | 1 | 3.75 | 1.296 | 480 | 2.3328
|  | Dec | 28 | 9 | 4.5 | 23.5 | 1.75 | 24 | 1.5 | -5.9 | -2.65 | 3.75 | 1.296 | 496 | -6.388
|  | TLgw-AMD (KWh) | [12 empty] | 84.3579
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 25°C
|  | Jan | 26.9 | 10.2 | 5.1 | 21.8 | 1.75 | 25 | 0.5 | -7.6 | -5.35 | 3.75 | 1.296 | 496 | -12.8965
|  | Feb | 31 | 10.6 | 5.3 | 25.7 | 1.75 | 25 | 0.5 | -3.7 | -1.45 | 3.75 | 1.296 | 448 | -3.1571
|  | Mar | 34.6 | 10.2 | 5.1 | 29.5 | 1.75 | 25 | 0.5 | 0.1 | 2.35 | 3.75 | 1.296 | 496 | 5.6648
|  | Apr | 36.8 | 9 | 4.5 | 32.3 | 1.75 | 25 | 0.5 | 2.9 | 5.15 | 3.75 | 1.296 | 480 | 12.0139
|  | May | 35.9 | 7.7 | 3.85 | 32.05 | 1.75 | 25 | 0.5 | 2.65 | 4.9 | 3.75 | 1.296 | 496 | 11.8117
|  | Jun | 35.1 | 5.7 | 2.85 | 32.25 | 1.75 | 25 | 0.5 | 2.85 | 5.1 | 3.75 | 1.296 | 480 | 11.8973
|  | Jul | 34 | 4.8 | 2.4 | 31.6 | 1.75 | 25 | 0.5 | 2.2 | 4.45 | 3.75 | 1.296 | 496 | 10.727
|  | Aug | 33.9 | 4.9 | 2.45 | 31.45 | 1.75 | 25 | 0.5 | 2.05 | 4.3 | 3.75 | 1.296 | 496 | 10.3654
|  | Sep | 34.1 | 5.3 | 2.65 | 31.45 | 1.75 | 25 | 0.5 | 2.05 | 4.3 | 3.75 | 1.296 | 480 | 10.031
|  | Oct | 33.8 | 6.4 | 3.2 | 30.6 | 1.75 | 25 | 0.5 | 1.2 | 3.45 | 3.75 | 1.296 | 496 | 8.3164
|  | Nov | 31.2 | 8.1 | 4.05 | 27.15 | 1.75 | 25 | 0.5 | -2.25 | 0 | 3.75 | 1.296 | 480 | 0
|  | Dec | 28 | 9 | 4.5 | 23.5 | 1.75 | 25 | 0.5 | -5.9 | -3.65 | 3.75 | 1.296 | 496 | -8.7985
|  | TLgw-DEL (KWh) | [12 empty] | 55.9755
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 26°C
|  | Jan | 26.9 | 10.2 | 5.1 | 21.8 | 1.75 | 26 | -0.5 | -7.6 | -6.35 | 3.75 | 1.296 | 496 | -15.3071
|  | Feb | 31 | 10.6 | 5.3 | 25.7 | 1.75 | 26 | -0.5 | -3.7 | -2.45 | 3.75 | 1.296 | 448 | -5.3343
|  | Mar | 34.6 | 10.2 | 5.1 | 29.5 | 1.75 | 26 | -0.5 | 0.1 | 1.35 | 3.75 | 1.296 | 496 | 3.2543
|  | Apr | 36.8 | 9 | 4.5 | 32.3 | 1.75 | 26 | -0.5 | 2.9 | 4.15 | 3.75 | 1.296 | 480 | 9.6811
|  | May | 35.9 | 7.7 | 3.85 | 32.05 | 1.75 | 26 | -0.5 | 2.65 | 3.9 | 3.75 | 1.296 | 496 | 9.4012
|  | Jun | 35.1 | 5.7 | 2.85 | 32.25 | 1.75 | 26 | -0.5 | 2.85 | 4.1 | 3.75 | 1.296 | 480 | 9.5645
|  | Jul | 34 | 4.8 | 2.4 | 31.6 | 1.75 | 26 | -0.5 | 2.2 | 3.45 | 3.75 | 1.296 | 496 | 8.3164
|  | Aug | 33.9 | 4.9 | 2.45 | 31.45 | 1.75 | 26 | -0.5 | 2.05 | 3.3 | 3.75 | 1.296 | 496 | 7.9548
|  | Sep | 34.1 | 5.3 | 2.65 | 31.45 | 1.75 | 26 | -0.5 | 2.05 | 3.3 | 3.75 | 1.296 | 480 | 7.6982
|  | Oct | 33.8 | 6.4 | 3.2 | 30.6 | 1.75 | 26 | -0.5 | 1.2 | 2.45 | 3.75 | 1.296 | 496 | 5.9059
|  | Nov | 31.2 | 8.1 | 4.05 | 27.15 | 1.75 | 26 | -0.5 | -2.25 | -1 | 3.75 | 1.296 | 480 | -2.3328
|  | Dec | 28 | 9 | 4.5 | 23.5 | 1.75 | 26 | -0.5 | -5.9 | -4.65 | 3.75 | 1.296 | 496 | -11.2091
|  | TLgw-DEL (KWh) | [12 empty] | 27.5931
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 27°C
|  | Jan | 26.9 | 10.2 | 5.1 | 21.8 | 1.75 | 27 | -1.5 | -7.6 | -7.35 | 3.75 | 1.296 | 496 | -17.7176
|  | Feb | 31 | 10.6 | 5.3 | 25.7 | 1.75 | 27 | -1.5 | -3.7 | -3.45 | 3.75 | 1.296 | 448 | -7.5116
|  | Mar | 34.6 | 10.2 | 5.1 | 29.5 | 1.75 | 27 | -1.5 | 0.1 | 0.35 | 3.75 | 1.296 | 496 | 0.8437
|  | Apr | 36.8 | 9 | 4.5 | 32.3 | 1.75 | 27 | -1.5 | 2.9 | 3.15 | 3.75 | 1.296 | 480 | 7.3483
|  | May | 35.9 | 7.7 | 3.85 | 32.05 | 1.75 | 27 | -1.5 | 2.65 | 2.9 | 3.75 | 1.296 | 496 | 6.9906
|  | Jun | 35.1 | 5.7 | 2.85 | 32.25 | 1.75 | 27 | -1.5 | 2.85 | 3.1 | 3.75 | 1.296 | 480 | 7.2317
|  | Jul | 34 | 4.8 | 2.4 | 31.6 | 1.75 | 27 | -1.5 | 2.2 | 2.45 | 3.75 | 1.296 | 496 | 5.9059
|  | Aug | 33.9 | 4.9 | 2.45 | 31.45 | 1.75 | 27 | -1.5 | 2.05 | 2.3 | 3.75 | 1.296 | 496 | 5.5443
|  | Sep | 34.1 | 5.3 | 2.65 | 31.45 | 1.75 | 27 | -1.5 | 2.05 | 2.3 | 3.75 | 1.296 | 480 | 5.3654
|  | Oct | 33.8 | 6.4 | 3.2 | 30.6 | 1.75 | 27 | -1.5 | 1.2 | 1.45 | 3.75 | 1.296 | 496 | 3.4953
|  | Nov | 31.2 | 8.1 | 4.05 | 27.15 | 1.75 | 27 | -1.5 | -2.25 | -2 | 3.75 | 1.296 | 480 | -4.6656
|  | Dec | 28 | 9 | 4.5 | 23.5 | 1.75 | 27 | -1.5 | -5.9 | -5.65 | 3.75 | 1.296 | 496 | -13.6197
|  | TLgw-DEL (KWh) | [12 empty] | -0.78926
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 28°C
|  | Jan | 26.9 | 10.2 | 5.1 | 21.8 | 1.75 | 28 | -2.5 | -7.6 | -8.35 | 3.75 | 1.296 | 496 | -20.1282
|  | Feb | 31 | 10.6 | 5.3 | 25.7 | 1.75 | 28 | -2.5 | -3.7 | -4.45 | 3.75 | 1.296 | 448 | -9.6889
|  | Mar | 34.6 | 10.2 | 5.1 | 29.5 | 1.75 | 28 | -2.5 | 0.1 | -0.65 | 3.75 | 1.296 | 496 | -1.5669
|  | Apr | 36.8 | 9 | 4.5 | 32.3 | 1.75 | 28 | -2.5 | 2.9 | 2.15 | 3.75 | 1.296 | 480 | 5.0155
|  | May | 35.9 | 7.7 | 3.85 | 32.05 | 1.75 | 28 | -2.5 | 2.65 | 1.9 | 3.75 | 1.296 | 496 | 4.5801
|  | Jun | 35.1 | 5.7 | 2.85 | 32.25 | 1.75 | 28 | -2.5 | 2.85 | 2.1 | 3.75 | 1.296 | 480 | 4.8989
|  | Jul | 34 | 4.8 | 2.4 | 31.6 | 1.75 | 28 | -2.5 | 2.2 | 1.45 | 3.75 | 1.296 | 496 | 3.4953
|  | Aug | 33.9 | 4.9 | 2.45 | 31.45 | 1.75 | 28 | -2.5 | 2.05 | 1.3 | 3.75 | 1.296 | 496 | 3.1337
|  | Sep | 34.1 | 5.3 | 2.65 | 31.45 | 1.75 | 28 | -2.5 | 2.05 | 1.3 | 3.75 | 1.296 | 480 | 3.0326
|  | Oct | 33.8 | 6.4 | 3.2 | 30.6 | 1.75 | 28 | -2.5 | 1.2 | 0.45 | 3.75 | 1.296 | 496 | 1.0848
|  | Nov | 31.2 | 8.1 | 4.05 | 27.15 | 1.75 | 28 | -2.5 | -2.25 | -3 | 3.75 | 1.296 | 480 | -6.9984
|  | Dec | 28 | 9 | 4.5 | 23.5 | 1.75 | 28 | -2.5 | -5.9 | -6.65 | 3.75 | 1.296 | 496 | -16.0302
|  | TLgw-DEL (KWh) | [12 empty] | -29.1717
Annual Radiation Thermal Load Through Glass Window
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jan | 0.55 | 0.51 | 85.17 | 1.296 | 496 | 15.357
|  | Feb | 0.55 | 0.51 | 94.63 | 1.296 | 448 | 15.4115
|  | Mar | 0.55 | 0.51 | 107.25 | 1.296 | 496 | 19.3382
|  | Apr | 0.55 | 0.51 | 116.71 | 1.296 | 480 | 20.3651
|  | May | 0.55 | 0.51 | 135.64 | 1.296 | 496 | 24.4572
|  | Jun | 0.55 | 0.51 | 173.5 | 1.296 | 480 | 30.2746
|  | Jul | 0.55 | 0.51 | 141.95 | 1.296 | 496 | 25.595
|  | Aug | 0.55 | 0.51 | 119.87 | 1.296 | 496 | 21.6137
|  | Sep | 0.55 | 0.51 | 110.41 | 1.296 | 480 | 19.2658
|  | Oct | 0.55 | 0.51 | 97.79 | 1.296 | 496 | 17.6325
|  | Nov | 0.55 | 0.51 | 85.17 | 1.296 | 480 | 14.8616
|  | Dec | 0.55 | 0.51 | 82.01 | 1.296 | 496 | 14.7872
|  | TLrad | [5 empty] | 238.9596
Inflitration Load for Different Setpoint Temperatures
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) |  | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 26.9 | 22 | 4.9 | 148.5382 |  | 0.277 | 41.1451 | 496 | 20.408
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31 | 22 | 9 | 272.8253 |  | 0.277 | 75.5726 | 448 | 33.8565
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 22 | 12.6 | 381.9554 |  | 0.277 | 105.8016 | 496 | 52.4776
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 22 | 14.8 | 448.646 |  | 0.277 | 124.2749 | 480 | 59.652
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 22 | 13.9 | 421.3635 |  | 0.277 | 116.7177 | 496 | 57.892
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 35.1 | 22 | 13.1 | 397.1123 |  | 0.277 | 110.0001 | 480 | 52.8001
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 22 | 12 | 363.767 |  | 0.277 | 100.7635 | 496 | 49.9787
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 22 | 11.9 | 360.7356 |  | 0.277 | 99.9238 | 496 | 49.5622
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 22 | 12.1 | 366.7984 |  | 0.277 | 101.6032 | 480 | 48.7695
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 22 | 11.8 | 357.7043 |  | 0.277 | 99.0841 | 496 | 49.1457
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 22 | 9.2 | 278.8881 |  | 0.277 | 77.252 | 480 | 37.081
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 28 | 22 | 6 | 181.8835 |  | 0.277 | 50.3817 | 496 | 24.9893
|  | Tinf for setpoint 22 degrees C | [12 empty] | 536.6125
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 26.9 | 23 | 3.9 | 118.2243 |  | 0.277 | 32.7481 | 496 | 16.2431
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31 | 23 | 8 | 242.5114 |  | 0.277 | 67.1756 | 448 | 30.0947
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 23 | 11.6 | 351.6415 |  | 0.277 | 97.4047 | 496 | 48.3127
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 23 | 13.8 | 418.3321 |  | 0.277 | 115.878 | 480 | 55.6214
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 23 | 12.9 | 391.0496 |  | 0.277 | 108.3207 | 496 | 53.7271
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 35.1 | 23 | 12.1 | 366.7984 |  | 0.277 | 101.6032 | 480 | 48.7695
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 23 | 11 | 333.4531 |  | 0.277 | 92.3665 | 496 | 45.8138
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 23 | 10.9 | 330.4217 |  | 0.277 | 91.5268 | 496 | 45.3973
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 23 | 11.1 | 336.4845 |  | 0.277 | 93.2062 | 480 | 44.739
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 23 | 10.8 | 327.3903 |  | 0.277 | 90.6871 | 496 | 44.9808
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 23 | 8.2 | 248.5741 |  | 0.277 | 68.855 | 480 | 33.0504
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 28 | 23 | 5 | 151.5696 |  | 0.277 | 41.9848 | 496 | 20.8245
|  | Tinf for setpoint 23 degrees C | [12 empty] | 487.5743
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 26.9 | 24 | 2.9 | 87.9104 |  | 0.277 | 24.3512 | 496 | 12.0782
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31 | 24 | 7 | 212.1974 |  | 0.277 | 58.7787 | 448 | 26.3329
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 24 | 10.6 | 321.3275 |  | 0.277 | 89.0077 | 496 | 44.1478
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 24 | 12.8 | 388.0182 |  | 0.277 | 107.481 | 480 | 51.5909
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 24 | 11.9 | 360.7356 |  | 0.277 | 99.9238 | 496 | 49.5622
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 35.1 | 24 | 11.1 | 336.4845 |  | 0.277 | 93.2062 | 480 | 44.739
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 24 | 10 | 303.1392 |  | 0.277 | 83.9696 | 496 | 41.6489
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 24 | 9.9 | 300.1078 |  | 0.277 | 83.1299 | 496 | 41.2324
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 24 | 10.1 | 306.1706 |  | 0.277 | 84.8093 | 480 | 40.7084
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 24 | 9.8 | 297.0764 |  | 0.277 | 82.2902 | 496 | 40.8159
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 24 | 7.2 | 218.2602 |  | 0.277 | 60.4581 | 480 | 29.0199
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 28 | 24 | 4 | 121.2557 |  | 0.277 | 33.5878 | 496 | 16.6596
|  | Tinf for setpoint 24 degrees C | [12 empty] | 438.536
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 26.9 | 25 | 1.9 | 57.5964 |  | 0.277 | 15.9542 | 496 | 7.9133
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31 | 25 | 6 | 181.8835 |  | 0.277 | 50.3817 | 448 | 22.571
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 25 | 9.6 | 291.0136 |  | 0.277 | 80.6108 | 496 | 39.9829
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 25 | 11.8 | 357.7043 |  | 0.277 | 99.0841 | 480 | 47.5604
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 25 | 10.9 | 330.4217 |  | 0.277 | 91.5268 | 496 | 45.3973
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 35.1 | 25 | 10.1 | 306.1706 |  | 0.277 | 84.8093 | 480 | 40.7084
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 25 | 9 | 272.8253 |  | 0.277 | 75.5726 | 496 | 37.484
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 25 | 8.9 | 269.7939 |  | 0.277 | 74.7329 | 496 | 37.0675
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 25 | 9.1 | 275.8567 |  | 0.277 | 76.4123 | 480 | 36.6779
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 25 | 8.8 | 266.7625 |  | 0.277 | 73.8932 | 496 | 36.651
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 25 | 6.2 | 187.9463 |  | 0.277 | 52.0611 | 480 | 24.9893
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 28 | 25 | 3 | 90.9418 |  | 0.277 | 25.1909 | 496 | 12.4947
|  | Tinf for setpoint 25 degrees C | [12 empty] | 389.4978
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 26.9 | 26 | 0.9 | 27.2825 |  | 0.277 | 7.5573 | 496 | 3.7484
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31 | 26 | 5 | 151.5696 |  | 0.277 | 41.9848 | 448 | 18.8092
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 26 | 8.6 | 260.6997 |  | 0.277 | 72.2138 | 496 | 35.8181
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 26 | 10.8 | 327.3903 |  | 0.277 | 90.6871 | 480 | 43.5298
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 26 | 9.9 | 300.1078 |  | 0.277 | 83.1299 | 496 | 41.2324
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 35.1 | 26 | 9.1 | 275.8567 |  | 0.277 | 76.4123 | 480 | 36.6779
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 26 | 8 | 242.5114 |  | 0.277 | 67.1756 | 496 | 33.3191
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 26 | 7.9 | 239.48 |  | 0.277 | 66.336 | 496 | 32.9026
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 26 | 8.1 | 245.5427 |  | 0.277 | 68.0153 | 480 | 32.6474
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 26 | 7.8 | 236.4486 |  | 0.277 | 65.4963 | 496 | 32.4861
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 26 | 5.2 | 157.6324 |  | 0.277 | 43.6642 | 480 | 20.9588
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 28 | 26 | 2 | 60.6278 |  | 0.277 | 16.7939 | 496 | 8.3298
|  | Tinf for setpoint 26 degrees C | [12 empty] | 340.4596
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 26.9 | 27 | -0.1 | -3.0314 |  | 0.277 | -0.8397 | 496 | -0.41649
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31 | 27 | 4 | 121.2557 |  | 0.277 | 33.5878 | 448 | 15.0473
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 27 | 7.6 | 230.3858 |  | 0.277 | 63.8169 | 496 | 31.6532
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 27 | 9.8 | 297.0764 |  | 0.277 | 82.2902 | 480 | 39.4993
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 27 | 8.9 | 269.7939 |  | 0.277 | 74.7329 | 496 | 37.0675
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 35.1 | 27 | 8.1 | 245.5427 |  | 0.277 | 68.0153 | 480 | 32.6474
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 27 | 7 | 212.1974 |  | 0.277 | 58.7787 | 496 | 29.1542
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 27 | 6.9 | 209.166 |  | 0.277 | 57.939 | 496 | 28.7377
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 27 | 7.1 | 215.2288 |  | 0.277 | 59.6184 | 480 | 28.6168
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 27 | 6.8 | 206.1347 |  | 0.277 | 57.0993 | 496 | 28.3213
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 27 | 4.2 | 127.3185 |  | 0.277 | 35.2672 | 480 | 16.9283
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 28 | 27 | 1 | 30.3139 |  | 0.277 | 8.397 | 496 | 4.1649
|  | Tinf for setpoint 27 degrees C | [12 empty] | 291.4214
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 26.9 | 28 | -1.1 | -33.3453 |  | 0.277 | -9.2367 | 496 | -4.5814
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31 | 28 | 3 | 90.9418 |  | 0.277 | 25.1909 | 448 | 11.2855
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 34.6 | 28 | 6.6 | 200.0719 |  | 0.277 | 55.4199 | 496 | 27.4883
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 36.8 | 28 | 8.8 | 266.7625 |  | 0.277 | 73.8932 | 480 | 35.4687
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 28 | 7.9 | 239.48 |  | 0.277 | 66.336 | 496 | 32.9026
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 35.1 | 28 | 7.1 | 215.2288 |  | 0.277 | 59.6184 | 480 | 28.6168
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 28 | 6 | 181.8835 |  | 0.277 | 50.3817 | 496 | 24.9893
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 28 | 5.9 | 178.8521 |  | 0.277 | 49.542 | 496 | 24.5729
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 28 | 6.1 | 184.9149 |  | 0.277 | 51.2214 | 480 | 24.5863
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.8 | 28 | 5.8 | 175.8207 |  | 0.277 | 48.7023 | 496 | 24.1564
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 28 | 3.2 | 97.0045 |  | 0.277 | 26.8703 | 480 | 12.8977
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 28 | 28 | 0 | 0 |  | 0.277 | 0 | 496 | 0
|  | Tinf for setpoint 28 degrees C | [12 empty] | 242.3832
Total Internal Load by People
|  | Month | People | SenL/person | CLF | SensL (W) | Latent/Person | LatentL (W) | Total peo L (W) | AC opn hrs |  | Total PL (KWh)
|  | Jan | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Feb | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 448 |  | 188.16
|  | Mar | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Apr | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | May | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Jun | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Jul | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Aug | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Sep | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Oct | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Nov | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Dec | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Total Internal Load by People | [9 empty] | 2452.8
Total Internal Heat Load of Lights per Year
|  | No. Bulbs | Watt Rating | bf | Fu | CLF | hrs (6hrs/day) | Tihlig(KWh)
|  | 3 | 60 | 1.24 | 0.66 | 0.8 | 2190 | 258.0906
|  | Total Internal Heat Load of Lights per Year | [5 empty] | 258.0906
Total Internal Heat Load-Equipment
|  | TV Rating W | Hrs /day | Total hrs | Tihe (KWh)
|  | 36 | 5 | 1825 | 65.7
|  | Total load Equipment |  |  | 65.7
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 22 | 141.1227 | 238.9596 | 536.6125 | 2452.8 | 258.0906 | 65.7 | 3693.2854
|  | 23 | 112.7403 | 238.9596 | 487.5743 | 2452.8 | 258.0906 | 65.7 | 3615.8648
|  | 24 | 84.3579 | 238.9596 | 438.536 | 2452.8 | 258.0906 | 65.7 | 3538.4442
|  | 25 | 55.9755 | 238.9596 | 389.4978 | 2452.8 | 258.0906 | 65.7 | 3461.0236
|  | 26 | 27.5931 | 238.9596 | 340.4596 | 2452.8 | 258.0906 | 65.7 | 3383.6029
|  | 27 | -0.78926 | 238.9596 | 291.4214 | 2452.8 | 258.0906 | 65.7 | 3306.1823
|  | 28 | -29.1717 | 238.9596 | 242.3832 | 2452.8 | 258.0906 | 65.7 | 3228.7617

## All Season Dengue Endemic_VN
Balance Point Temperature, Annual Variable Degree Days, Thermal Load of Living Space and Annual Electricity Consumption Calculations for Chennai- Baseline and Solar Electricity Scenarios
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | AC hrs/24 hrs (fAC) | Conv (24/1000) KWh |  |  | Annual VCDD |  |  |  | Annual VCDD |  |  |  | Annual VCDD |  | All Other Heat Loads | BE+Other Loads | 10%SF |  | EER | Elec. Cons.
|  | Jan | 22 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9605 | 19 | 244.7 | [21 empty] | LDRZ Setpoint Adjsuted Preference %
|  | Feb | 22 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9434 | 19 | 249.4 | [21 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Mar | 22 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9319 | 19 | 318.8 | [21 empty] | 22 | 16 | 0.34783
|  | Apr | 22 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.909 | 19 | 335.3 | [21 empty] | 23 | 10 | 0.21739
|  | May | 22 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8347 | 19 | 372.4 | [21 empty] | 24 | 20 | 0.43478
|  | Jun | 22 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.7545 | 19 | 321 | [22 empty] | 46
|  | July | 22 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8175 | 19 | 289.1
|  | Aug | 22 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8976 | 19 | 316.1
|  | Sep | 22 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9262 | 19 | 270.3
|  | Oct | 22 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9434 | 19 | 275.9
|  | Nov | 22 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9605 | 19 | 284.5
|  | Dec | 22 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9662 | 19 | 252.4
|  | Annual VCDD | [9 empty] | 3529.9 | 0.66667 | 0.024 | 3.59 | 12.96 | 3529.9 | 2627.7366 | 3.94 | 12.96 | 3529.9 | 2883.9227 | 2.13 | 41.904 | 3529.9 | 5041.009 | 3777.1348 | 14329.8031 | 1432.9803 | 15762.7834 | 3.1 | 5085 | 22
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 23 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9605 | 20 | 213.7
|  | Feb | 23 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9434 | 20 | 221.4
|  | Mar | 23 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9319 | 20 | 287.8
|  | Apr | 23 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.909 | 20 | 305.3
|  | May | 23 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8347 | 20 | 341.4
|  | Jun | 23 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.7545 | 20 | 291
|  | July | 23 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8175 | 20 | 258.1
|  | Aug | 23 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8976 | 20 | 285.1
|  | Sep | 23 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9262 | 20 | 240.3
|  | Oct | 23 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9434 | 20 | 244.9
|  | Nov | 23 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9605 | 20 | 254.5
|  | Dec | 23 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9662 | 20 | 221.4
|  | Annual VCDD | [9 empty] | 3164.9 | 0.66667 | 0.024 | 3.59 | 12.96 | 3164.9 | 2356.0225 | 3.94 | 12.96 | 3164.9 | 2585.7182 | 2.13 | 41.904 | 3164.9 | 4519.7567 | 3699.7142 | 13161.2116 | 1316.1212 | 14477.3328 | 3.1 | 4670 | 23
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 24 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9605 | 21 | 183.1
|  | Feb | 24 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9434 | 21 | 193.4
|  | Mar | 24 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9319 | 21 | 256.8
|  | Apr | 24 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.909 | 21 | 275.3
|  | May | 24 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8347 | 21 | 310.4
|  | Jun | 24 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.7545 | 21 | 261
|  | Jul | 24 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8175 | 21 | 227.1
|  | Aug | 24 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8976 | 21 | 254.1
|  | Sep | 24 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9262 | 21 | 210.3
|  | Oct | 24 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9434 | 21 | 213.9
|  | Nov | 24 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9605 | 21 | 224.5
|  | Dec | 24 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9662 | 21 | 190.4
|  | Annual VCDD | [9 empty] | 2800.3 | 0.66667 | 0.024 | 3.59 | 12.96 | 2800.3 | 2084.606 | 3.94 | 12.96 | 2800.3 | 2287.8406 | 2.13 | 41.904 | 2800.3 | 3999.0757 | 3622.2936 | 11993.816 | 1199.3816 | 13193.1976 | 3.1 | 4256 | 24
|  | Avg Energy Consumption of AC Unit for LDRZ | [29 empty] | 4634.3478
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | [21 empty] | MDRZ Setpoint Adjsuted Preference %
|  | Jan | 25 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9605 | 22 | 153.2 | [21 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Feb | 25 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9434 | 22 | 165.5 | [21 empty] | 25 | 12 | 100
|  | Mar | 25 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9319 | 22 | 225.8
|  | Apr | 25 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.909 | 22 | 245.3
|  | May | 25 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8347 | 22 | 279.4
|  | Jun | 25 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.7545 | 22 | 231
|  | Jul | 25 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8175 | 22 | 196.1
|  | Aug | 25 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8976 | 22 | 223.1
|  | Sep | 25 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9262 | 22 | 180.3
|  | Oct | 25 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9434 | 22 | 182.9
|  | Nov | 25 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9605 | 22 | 194.5
|  | Dec | 25 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9662 | 22 | 159.7
|  | Annual VCDD | [9 empty] | 2436.8 | 0.66667 | 0.024 | 3.59 | 12.96 | 2436.8 | 1814.0085 | 3.94 | 12.96 | 2436.8 | 1990.8617 | 2.13 | 41.904 | 2436.8 | 3479.9656 | 3544.873 | 10829.7088 | 1082.9709 | 11912.6797 | 3.1 | 3843 | 25
|  | Avg Energy Consumption of AC Unit for MDRZ | [29 empty] | 3843
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 26 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9605 | 23 | 124.8
|  | Feb | 26 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9434 | 23 | 138
|  | Mar | 26 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9319 | 23 | 194.8
|  | Apr | 26 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.909 | 23 | 215.3
|  | May | 26 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8347 | 23 | 248.4
|  | Jun | 26 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.7545 | 23 | 201
|  | July | 26 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8175 | 23 | 165.1
|  | Aug | 26 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8976 | 23 | 192.1
|  | Sep | 26 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9262 | 23 | 150.3
|  | Oct | 26 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9434 | 23 | 152
|  | Nov | 26 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9605 | 23 | 164.5
|  | Dec | 26 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9662 | 23 | 129.6
|  | Annual VCDD | [9 empty] | 2075.9 | 0.66667 | 0.024 | 3.59 | 12.96 | 2075.9 | 1545.3465 | 3.94 | 12.96 | 2075.9 | 1696.007 | 2.13 | 41.904 | 2075.9 | 2964.5685 | 3467.4523 | 9673.3743 | 967.3374 | 10640.7118 | 3.1 | 3432 | 26
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 27 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9605 | 24 | 98.3 | [21 empty] | HDRZ Setpoint Adjsuted Preference %
|  | Feb | 27 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9434 | 24 | 111.2 | [21 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Mar | 27 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9319 | 24 | 163.8 | [21 empty] | 26 | 10 | 0.5
|  | Apr | 27 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.909 | 24 | 185.3 | [21 empty] | 27 | 8 | 0.4
|  | May | 27 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8347 | 24 | 217.4 | [21 empty] | 28 | 2 | 0.1
|  | Jun | 27 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.7545 | 24 | 171 | [22 empty] | 20
|  | Jul | 27 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8175 | 24 | 134.1
|  | Aug | 27 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8976 | 24 | 161.1
|  | Sep | 27 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9262 | 24 | 120.3
|  | Oct | 27 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9434 | 24 | 121.1
|  | Nov | 27 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9605 | 24 | 134.7
|  | Dec | 27 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9662 | 24 | 100.6
|  | Annual VCDD | [9 empty] | 1718.9 | 0.66667 | 0.024 | 3.59 | 12.96 | 1718.9 | 1279.5877 | 3.94 | 12.96 | 1718.9 | 1404.3385 | 2.13 | 41.904 | 1718.9 | 2454.741 | 3390.0317 | 8528.699 | 852.8699 | 9381.5688 | 3.1 | 3026 | 27
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 28 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9605 | 25 | 74.3
|  | Feb | 28 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9434 | 25 | 86.2
|  | Mar | 28 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9319 | 25 | 133.2
|  | Apr | 28 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.909 | 25 | 155.3
|  | May | 28 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8347 | 25 | 186.5
|  | Jun | 28 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.7545 | 25 | 141.1
|  | Jul | 28 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8175 | 25 | 103.3
|  | Aug | 28 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8976 | 25 | 130.4
|  | Sep | 28 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9262 | 25 | 90.8
|  | Oct | 28 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9434 | 25 | 91
|  | Nov | 28 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9605 | 25 | 105.3
|  | Dec | 28 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9662 | 25 | 73.6
|  | Annual VCDD | [9 empty] | 1371 | 0.66667 | 0.024 | 3.59 | 12.96 | 1371 | 1020.6031 | 3.94 | 12.96 | 1371 | 1120.1048 | 2.13 | 41.904 | 1371 | 1957.9091 | 3312.6111 | 7411.2281 | 741.1228 | 8152.3509 | 3.1 | 2630 | 28
|  | Avg Energy Consumption of AC Unit for HDRZ | [29 empty] | 3189
CLTDgw-avg (°C) for AC Opn hrs. |  | Thermal Conductive Load (TLgw-x) Calculated for Three Climate Zones
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 22°C
AC Opn hrs. | CLTDgw (°C) | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
00.00-01.00 | 1 | Jan | 33.1 | 9.6 | 4.8 | 28.3 | 1.75 | 22 | 3.5 | -1.1 | 4.15 | 3.75 | 1.296 | 496 | 10.0038
01.00-02.00 | 1 | Feb | 34 | 10 | 5 | 29 | 1.75 | 22 | 3.5 | -0.4 | 4.85 | 3.75 | 1.296 | 448 | 10.5598
02.00-03.00 | 0 | Mar | 35 | 9.3 | 4.65 | 30.35 | 1.75 | 22 | 3.5 | 0.95 | 6.2 | 3.75 | 1.296 | 496 | 14.9455
03.00-04.00 | -1 | Apr | 35.5 | 8.6 | 4.3 | 31.2 | 1.75 | 22 | 3.5 | 1.8 | 7.05 | 3.75 | 1.296 | 480 | 16.4462
04.00-05.00 | -1 | May | 35.7 | 8.4 | 4.2 | 31.5 | 1.75 | 22 | 3.5 | 2.1 | 7.35 | 3.75 | 1.296 | 496 | 17.7176
05.00-06.00 | -1 | Jun | 34.1 | 8 | 4 | 30.1 | 1.75 | 22 | 3.5 | 0.7 | 5.95 | 3.75 | 1.296 | 480 | 13.8802
06.00-07.00 | -1 | Jul | 33.2 | 7.8 | 3.9 | 29.3 | 1.75 | 22 | 3.5 | -0.1 | 5.15 | 3.75 | 1.296 | 496 | 12.4144
07.00-08.00 | -1 | Aug | 33.2 | 7.6 | 3.8 | 29.4 | 1.75 | 22 | 3.5 | 0 | 5.25 | 3.75 | 1.296 | 496 | 12.6554
08.00-09.00 | 0 | Sep | 33.1 | 7.5 | 3.75 | 29.35 | 1.75 | 22 | 3.5 | -0.05 | 5.2 | 3.75 | 1.296 | 480 | 12.1306
17.00-18.00 | 7 | Oct | 32.9 | 7.7 | 3.85 | 29.05 | 1.75 | 22 | 3.5 | -0.35 | 4.9 | 3.75 | 1.296 | 496 | 11.8117
18.00-19.00 | 7 | Nov | 33 | 8.2 | 4.1 | 28.9 | 1.75 | 22 | 3.5 | -0.5 | 4.75 | 3.75 | 1.296 | 480 | 11.0808
19.00-20.00 | 6 | Dec | 32.9 | 8.8 | 4.4 | 28.5 | 1.75 | 22 | 3.5 | -0.9 | 4.35 | 3.75 | 1.296 | 496 | 10.4859
20.00-21.00 | 4 | TLgw-CHN (KWh) | [12 empty] | 154.132
21.00-22.00 | 3 | Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 23°C
22.00-23.00 | 2 | Jan | 33.1 | 9.6 | 4.8 | 28.3 | 1.75 | 23 | 2.5 | -1.1 | 3.15 | 3.75 | 1.296 | 496 | 7.5933
23.00-00.00 | 2 | Feb | 34 | 10 | 5 | 29 | 1.75 | 23 | 2.5 | -0.4 | 3.85 | 3.75 | 1.296 | 448 | 8.3825
CLTDgw-avg (°C) | 1.75 | Mar | 35 | 9.3 | 4.65 | 30.35 | 1.75 | 23 | 2.5 | 0.95 | 5.2 | 3.75 | 1.296 | 496 | 12.5349
|  | Apr | 35.5 | 8.6 | 4.3 | 31.2 | 1.75 | 23 | 2.5 | 1.8 | 6.05 | 3.75 | 1.296 | 480 | 14.1134
|  | May | 35.7 | 8.4 | 4.2 | 31.5 | 1.75 | 23 | 2.5 | 2.1 | 6.35 | 3.75 | 1.296 | 496 | 15.3071
|  | Jun | 34.1 | 8 | 4 | 30.1 | 1.75 | 23 | 2.5 | 0.7 | 4.95 | 3.75 | 1.296 | 480 | 11.5474
|  | Jul | 33.2 | 7.8 | 3.9 | 29.3 | 1.75 | 23 | 2.5 | -0.1 | 4.15 | 3.75 | 1.296 | 496 | 10.0038
|  | Aug | 33.2 | 7.6 | 3.8 | 29.4 | 1.75 | 23 | 2.5 | 0 | 4.25 | 3.75 | 1.296 | 496 | 10.2449
|  | Sep | 33.1 | 7.5 | 3.75 | 29.35 | 1.75 | 23 | 2.5 | -0.05 | 4.2 | 3.75 | 1.296 | 480 | 9.7978
|  | Oct | 32.9 | 7.7 | 3.85 | 29.05 | 1.75 | 23 | 2.5 | -0.35 | 3.9 | 3.75 | 1.296 | 496 | 9.4012
|  | Nov | 33 | 8.2 | 4.1 | 28.9 | 1.75 | 23 | 2.5 | -0.5 | 3.75 | 3.75 | 1.296 | 480 | 8.748
|  | Dec | 32.9 | 8.8 | 4.4 | 28.5 | 1.75 | 23 | 2.5 | -0.9 | 3.35 | 3.75 | 1.296 | 496 | 8.0754
|  | TLgw-CHN (KWh) | [12 empty] | 125.7496
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 24°C
|  | Jan | 33.1 | 9.6 | 4.8 | 28.3 | 1.75 | 24 | 1.5 | -1.1 | 2.15 | 3.75 | 1.296 | 496 | 5.1827
|  | Feb | 34 | 10 | 5 | 29 | 1.75 | 24 | 1.5 | -0.4 | 2.85 | 3.75 | 1.296 | 448 | 6.2052
|  | Mar | 35 | 9.3 | 4.65 | 30.35 | 1.75 | 24 | 1.5 | 0.95 | 4.2 | 3.75 | 1.296 | 496 | 10.1244
|  | Apr | 35.5 | 8.6 | 4.3 | 31.2 | 1.75 | 24 | 1.5 | 1.8 | 5.05 | 3.75 | 1.296 | 480 | 11.7806
|  | May | 35.7 | 8.4 | 4.2 | 31.5 | 1.75 | 24 | 1.5 | 2.1 | 5.35 | 3.75 | 1.296 | 496 | 12.8965
|  | Jun | 34.1 | 8 | 4 | 30.1 | 1.75 | 24 | 1.5 | 0.7 | 3.95 | 3.75 | 1.296 | 480 | 9.2146
|  | Jul | 33.2 | 7.8 | 3.9 | 29.3 | 1.75 | 24 | 1.5 | -0.1 | 3.15 | 3.75 | 1.296 | 496 | 7.5933
|  | Aug | 33.2 | 7.6 | 3.8 | 29.4 | 1.75 | 24 | 1.5 | 0 | 3.25 | 3.75 | 1.296 | 496 | 7.8343
|  | Sep | 33.1 | 7.5 | 3.75 | 29.35 | 1.75 | 24 | 1.5 | -0.05 | 3.2 | 3.75 | 1.296 | 480 | 7.465
|  | Oct | 32.9 | 7.7 | 3.85 | 29.05 | 1.75 | 24 | 1.5 | -0.35 | 2.9 | 3.75 | 1.296 | 496 | 6.9906
|  | Nov | 33 | 8.2 | 4.1 | 28.9 | 1.75 | 24 | 1.5 | -0.5 | 2.75 | 3.75 | 1.296 | 480 | 6.4152
|  | Dec | 32.9 | 8.8 | 4.4 | 28.5 | 1.75 | 24 | 1.5 | -0.9 | 2.35 | 3.75 | 1.296 | 496 | 5.6648
|  | TLgw-AMD (KWh) | [12 empty] | 97.3672
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 25°C
|  | Jan | 33.1 | 9.6 | 4.8 | 28.3 | 1.75 | 25 | 0.5 | -1.1 | 1.15 | 3.75 | 1.296 | 496 | 2.7721
|  | Feb | 34 | 10 | 5 | 29 | 1.75 | 25 | 0.5 | -0.4 | 1.85 | 3.75 | 1.296 | 448 | 4.028
|  | Mar | 35 | 9.3 | 4.65 | 30.35 | 1.75 | 25 | 0.5 | 0.95 | 3.2 | 3.75 | 1.296 | 496 | 7.7138
|  | Apr | 35.5 | 8.6 | 4.3 | 31.2 | 1.75 | 25 | 0.5 | 1.8 | 4.05 | 3.75 | 1.296 | 480 | 9.4478
|  | May | 35.7 | 8.4 | 4.2 | 31.5 | 1.75 | 25 | 0.5 | 2.1 | 4.35 | 3.75 | 1.296 | 496 | 10.4859
|  | Jun | 34.1 | 8 | 4 | 30.1 | 1.75 | 25 | 0.5 | 0.7 | 2.95 | 3.75 | 1.296 | 480 | 6.8818
|  | Jul | 33.2 | 7.8 | 3.9 | 29.3 | 1.75 | 25 | 0.5 | -0.1 | 2.15 | 3.75 | 1.296 | 496 | 5.1827
|  | Aug | 33.2 | 7.6 | 3.8 | 29.4 | 1.75 | 25 | 0.5 | 0 | 2.25 | 3.75 | 1.296 | 496 | 5.4238
|  | Sep | 33.1 | 7.5 | 3.75 | 29.35 | 1.75 | 25 | 0.5 | -0.05 | 2.2 | 3.75 | 1.296 | 480 | 5.1322
|  | Oct | 32.9 | 7.7 | 3.85 | 29.05 | 1.75 | 25 | 0.5 | -0.35 | 1.9 | 3.75 | 1.296 | 496 | 4.5801
|  | Nov | 33 | 8.2 | 4.1 | 28.9 | 1.75 | 25 | 0.5 | -0.5 | 1.75 | 3.75 | 1.296 | 480 | 4.0824
|  | Dec | 32.9 | 8.8 | 4.4 | 28.5 | 1.75 | 25 | 0.5 | -0.9 | 1.35 | 3.75 | 1.296 | 496 | 3.2543
|  | TLgw-DEL (KWh) | [12 empty] | 68.9848
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 26°C
|  | Jan | 33.1 | 9.6 | 4.8 | 28.3 | 1.75 | 26 | -0.5 | -1.1 | 0.15 | 3.75 | 1.296 | 496 | 0.36158
|  | Feb | 34 | 10 | 5 | 29 | 1.75 | 26 | -0.5 | -0.4 | 0.85 | 3.75 | 1.296 | 448 | 1.8507
|  | Mar | 35 | 9.3 | 4.65 | 30.35 | 1.75 | 26 | -0.5 | 0.95 | 2.2 | 3.75 | 1.296 | 496 | 5.3032
|  | Apr | 35.5 | 8.6 | 4.3 | 31.2 | 1.75 | 26 | -0.5 | 1.8 | 3.05 | 3.75 | 1.296 | 480 | 7.115
|  | May | 35.7 | 8.4 | 4.2 | 31.5 | 1.75 | 26 | -0.5 | 2.1 | 3.35 | 3.75 | 1.296 | 496 | 8.0754
|  | Jun | 34.1 | 8 | 4 | 30.1 | 1.75 | 26 | -0.5 | 0.7 | 1.95 | 3.75 | 1.296 | 480 | 4.549
|  | Jul | 33.2 | 7.8 | 3.9 | 29.3 | 1.75 | 26 | -0.5 | -0.1 | 1.15 | 3.75 | 1.296 | 496 | 2.7721
|  | Aug | 33.2 | 7.6 | 3.8 | 29.4 | 1.75 | 26 | -0.5 | 0 | 1.25 | 3.75 | 1.296 | 496 | 3.0132
|  | Sep | 33.1 | 7.5 | 3.75 | 29.35 | 1.75 | 26 | -0.5 | -0.05 | 1.2 | 3.75 | 1.296 | 480 | 2.7994
|  | Oct | 32.9 | 7.7 | 3.85 | 29.05 | 1.75 | 26 | -0.5 | -0.35 | 0.9 | 3.75 | 1.296 | 496 | 2.1695
|  | Nov | 33 | 8.2 | 4.1 | 28.9 | 1.75 | 26 | -0.5 | -0.5 | 0.75 | 3.75 | 1.296 | 480 | 1.7496
|  | Dec | 32.9 | 8.8 | 4.4 | 28.5 | 1.75 | 26 | -0.5 | -0.9 | 0.35 | 3.75 | 1.296 | 496 | 0.8437
|  | TLgw-DEL (KWh) | [12 empty] | 40.6024
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 27°C
|  | Jan | 33.1 | 9.6 | 4.8 | 28.3 | 1.75 | 27 | -1.5 | -1.1 | -0.85 | 3.75 | 1.296 | 496 | -2.049
|  | Feb | 34 | 10 | 5 | 29 | 1.75 | 27 | -1.5 | -0.4 | -0.15 | 3.75 | 1.296 | 448 | -0.32659
|  | Mar | 35 | 9.3 | 4.65 | 30.35 | 1.75 | 27 | -1.5 | 0.95 | 1.2 | 3.75 | 1.296 | 496 | 2.8927
|  | Apr | 35.5 | 8.6 | 4.3 | 31.2 | 1.75 | 27 | -1.5 | 1.8 | 2.05 | 3.75 | 1.296 | 480 | 4.7822
|  | May | 35.7 | 8.4 | 4.2 | 31.5 | 1.75 | 27 | -1.5 | 2.1 | 2.35 | 3.75 | 1.296 | 496 | 5.6648
|  | Jun | 34.1 | 8 | 4 | 30.1 | 1.75 | 27 | -1.5 | 0.7 | 0.95 | 3.75 | 1.296 | 480 | 2.2162
|  | Jul | 33.2 | 7.8 | 3.9 | 29.3 | 1.75 | 27 | -1.5 | -0.1 | 0.15 | 3.75 | 1.296 | 496 | 0.36158
|  | Aug | 33.2 | 7.6 | 3.8 | 29.4 | 1.75 | 27 | -1.5 | 0 | 0.25 | 3.75 | 1.296 | 496 | 0.60264
|  | Sep | 33.1 | 7.5 | 3.75 | 29.35 | 1.75 | 27 | -1.5 | -0.05 | 0.2 | 3.75 | 1.296 | 480 | 0.46656
|  | Oct | 32.9 | 7.7 | 3.85 | 29.05 | 1.75 | 27 | -1.5 | -0.35 | -0.1 | 3.75 | 1.296 | 496 | -0.24106
|  | Nov | 33 | 8.2 | 4.1 | 28.9 | 1.75 | 27 | -1.5 | -0.5 | -0.25 | 3.75 | 1.296 | 480 | -0.5832
|  | Dec | 32.9 | 8.8 | 4.4 | 28.5 | 1.75 | 27 | -1.5 | -0.9 | -0.65 | 3.75 | 1.296 | 496 | -1.5669
|  | TLgw-DEL (KWh) | [12 empty] | 12.22
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 28°C
|  | Jan | 33.1 | 9.6 | 4.8 | 28.3 | 1.75 | 28 | -2.5 | -1.1 | -1.85 | 3.75 | 1.296 | 496 | -4.4595
|  | Feb | 34 | 10 | 5 | 29 | 1.75 | 28 | -2.5 | -0.4 | -1.15 | 3.75 | 1.296 | 448 | -2.5039
|  | Mar | 35 | 9.3 | 4.65 | 30.35 | 1.75 | 28 | -2.5 | 0.95 | 0.2 | 3.75 | 1.296 | 496 | 0.48211
|  | Apr | 35.5 | 8.6 | 4.3 | 31.2 | 1.75 | 28 | -2.5 | 1.8 | 1.05 | 3.75 | 1.296 | 480 | 2.4494
|  | May | 35.7 | 8.4 | 4.2 | 31.5 | 1.75 | 28 | -2.5 | 2.1 | 1.35 | 3.75 | 1.296 | 496 | 3.2543
|  | Jun | 34.1 | 8 | 4 | 30.1 | 1.75 | 28 | -2.5 | 0.7 | -0.05 | 3.75 | 1.296 | 480 | -0.11664
|  | Jul | 33.2 | 7.8 | 3.9 | 29.3 | 1.75 | 28 | -2.5 | -0.1 | -0.85 | 3.75 | 1.296 | 496 | -2.049
|  | Aug | 33.2 | 7.6 | 3.8 | 29.4 | 1.75 | 28 | -2.5 | 0 | -0.75 | 3.75 | 1.296 | 496 | -1.8079
|  | Sep | 33.1 | 7.5 | 3.75 | 29.35 | 1.75 | 28 | -2.5 | -0.05 | -0.8 | 3.75 | 1.296 | 480 | -1.8662
|  | Oct | 32.9 | 7.7 | 3.85 | 29.05 | 1.75 | 28 | -2.5 | -0.35 | -1.1 | 3.75 | 1.296 | 496 | -2.6516
|  | Nov | 33 | 8.2 | 4.1 | 28.9 | 1.75 | 28 | -2.5 | -0.5 | -1.25 | 3.75 | 1.296 | 480 | -2.916
|  | Dec | 32.9 | 8.8 | 4.4 | 28.5 | 1.75 | 28 | -2.5 | -0.9 | -1.65 | 3.75 | 1.296 | 496 | -3.9774
|  | TLgw-DEL (KWh) | [12 empty] | -16.1624
Annual Radiation Thermal Load Through Glass Window
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jan | 0.55 | 0.51 | 94.63 | 1.296 | 496 | 17.0627
|  | Feb | 0.55 | 0.51 | 104.1 | 1.296 | 448 | 16.9538
|  | Mar | 0.55 | 0.51 | 110.41 | 1.296 | 496 | 19.908
|  | Apr | 0.55 | 0.51 | 123.02 | 1.296 | 480 | 21.4662
|  | May | 0.55 | 0.51 | 164.03 | 1.296 | 496 | 29.5762
|  | Jun | 0.55 | 0.51 | 208.2 | 1.296 | 480 | 36.3295
|  | Jul | 0.55 | 0.51 | 173.5 | 1.296 | 496 | 31.2838
|  | Aug | 0.55 | 0.51 | 129.33 | 1.296 | 496 | 23.3195
|  | Sep | 0.55 | 0.51 | 113.56 | 1.296 | 480 | 19.8155
|  | Oct | 0.55 | 0.51 | 104.1 | 1.296 | 496 | 18.7703
|  | Nov | 0.55 | 0.51 | 94.63 | 1.296 | 480 | 16.5123
|  | Dec | 0.55 | 0.51 | 91.48 | 1.296 | 496 | 16.4947
|  | TLrad | [5 empty] | 267.4925
Inflitration Load for Different Setpoint Temperatures
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) |  | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 22 | 11.1 | 336.4845 |  | 0.277 | 93.2062 | 496 | 46.2303
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 22 | 12 | 363.767 |  | 0.277 | 100.7635 | 448 | 45.142
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 22 | 13 | 394.081 |  | 0.277 | 109.1604 | 496 | 54.1436
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 35.5 | 22 | 13.5 | 409.2379 |  | 0.277 | 113.3589 | 480 | 54.4123
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.7 | 22 | 13.7 | 415.3007 |  | 0.277 | 115.0383 | 496 | 57.059
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 22 | 12.1 | 366.7984 |  | 0.277 | 101.6032 | 480 | 48.7695
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 22 | 11.2 | 339.5159 |  | 0.277 | 94.0459 | 496 | 46.6468
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 22 | 11.2 | 339.5159 |  | 0.277 | 94.0459 | 496 | 46.6468
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 22 | 11.1 | 336.4845 |  | 0.277 | 93.2062 | 480 | 44.739
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 22 | 10.9 | 330.4217 |  | 0.277 | 91.5268 | 496 | 45.3973
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33 | 22 | 11 | 333.4531 |  | 0.277 | 92.3665 | 480 | 44.3359
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 22 | 10.9 | 330.4217 |  | 0.277 | 91.5268 | 496 | 45.3973
|  | Tinf for setpoint 22 degrees C | [12 empty] | 578.9197
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 23 | 10.1 | 306.1706 |  | 0.277 | 84.8093 | 496 | 42.0654
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 23 | 11 | 333.4531 |  | 0.277 | 92.3665 | 448 | 41.3802
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 23 | 12 | 363.767 |  | 0.277 | 100.7635 | 496 | 49.9787
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 35.5 | 23 | 12.5 | 378.924 |  | 0.277 | 104.9619 | 480 | 50.3817
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.7 | 23 | 12.7 | 384.9868 |  | 0.277 | 106.6413 | 496 | 52.8941
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 23 | 11.1 | 336.4845 |  | 0.277 | 93.2062 | 480 | 44.739
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 23 | 10.2 | 309.202 |  | 0.277 | 85.6489 | 496 | 42.4819
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 23 | 10.2 | 309.202 |  | 0.277 | 85.6489 | 496 | 42.4819
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 23 | 10.1 | 306.1706 |  | 0.277 | 84.8093 | 480 | 40.7084
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 23 | 9.9 | 300.1078 |  | 0.277 | 83.1299 | 496 | 41.2324
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33 | 23 | 10 | 303.1392 |  | 0.277 | 83.9696 | 480 | 40.3054
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 23 | 9.9 | 300.1078 |  | 0.277 | 83.1299 | 496 | 41.2324
|  | Tinf for setpoint 23 degrees C | [12 empty] | 529.8815
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 24 | 9.1 | 275.8567 |  | 0.277 | 76.4123 | 496 | 37.9005
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 24 | 10 | 303.1392 |  | 0.277 | 83.9696 | 448 | 37.6184
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 24 | 11 | 333.4531 |  | 0.277 | 92.3665 | 496 | 45.8138
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 35.5 | 24 | 11.5 | 348.6101 |  | 0.277 | 96.565 | 480 | 46.3512
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.7 | 24 | 11.7 | 354.6729 |  | 0.277 | 98.2444 | 496 | 48.7292
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 24 | 10.1 | 306.1706 |  | 0.277 | 84.8093 | 480 | 40.7084
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 24 | 9.2 | 278.8881 |  | 0.277 | 77.252 | 496 | 38.317
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 24 | 9.2 | 278.8881 |  | 0.277 | 77.252 | 496 | 38.317
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 24 | 9.1 | 275.8567 |  | 0.277 | 76.4123 | 480 | 36.6779
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 24 | 8.9 | 269.7939 |  | 0.277 | 74.7329 | 496 | 37.0675
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33 | 24 | 9 | 272.8253 |  | 0.277 | 75.5726 | 480 | 36.2748
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 24 | 8.9 | 269.7939 |  | 0.277 | 74.7329 | 496 | 37.0675
|  | Tinf for setpoint 24 degrees C | [12 empty] | 480.8433
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 25 | 8.1 | 245.5427 |  | 0.277 | 68.0153 | 496 | 33.7356
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 25 | 9 | 272.8253 |  | 0.277 | 75.5726 | 448 | 33.8565
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 25 | 10 | 303.1392 |  | 0.277 | 83.9696 | 496 | 41.6489
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 35.5 | 25 | 10.5 | 318.2962 |  | 0.277 | 88.168 | 480 | 42.3207
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.7 | 25 | 10.7 | 324.3589 |  | 0.277 | 89.8474 | 496 | 44.5643
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 25 | 9.1 | 275.8567 |  | 0.277 | 76.4123 | 480 | 36.6779
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 25 | 8.2 | 248.5741 |  | 0.277 | 68.855 | 496 | 34.1521
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 25 | 8.2 | 248.5741 |  | 0.277 | 68.855 | 496 | 34.1521
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 25 | 8.1 | 245.5427 |  | 0.277 | 68.0153 | 480 | 32.6474
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 25 | 7.9 | 239.48 |  | 0.277 | 66.336 | 496 | 32.9026
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33 | 25 | 8 | 242.5114 |  | 0.277 | 67.1756 | 480 | 32.2443
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 25 | 7.9 | 239.48 |  | 0.277 | 66.336 | 496 | 32.9026
|  | Tinf for setpoint 25 degrees C | [12 empty] | 431.8051
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 26 | 7.1 | 215.2288 |  | 0.277 | 59.6184 | 496 | 29.5707
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 26 | 8 | 242.5114 |  | 0.277 | 67.1756 | 448 | 30.0947
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 26 | 9 | 272.8253 |  | 0.277 | 75.5726 | 496 | 37.484
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 35.5 | 26 | 9.5 | 287.9822 |  | 0.277 | 79.7711 | 480 | 38.2901
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.7 | 26 | 9.7 | 294.045 |  | 0.277 | 81.4505 | 496 | 40.3994
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 26 | 8.1 | 245.5427 |  | 0.277 | 68.0153 | 480 | 32.6474
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 26 | 7.2 | 218.2602 |  | 0.277 | 60.4581 | 496 | 29.9872
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 26 | 7.2 | 218.2602 |  | 0.277 | 60.4581 | 496 | 29.9872
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 26 | 7.1 | 215.2288 |  | 0.277 | 59.6184 | 480 | 28.6168
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 26 | 6.9 | 209.166 |  | 0.277 | 57.939 | 496 | 28.7377
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33 | 26 | 7 | 212.1974 |  | 0.277 | 58.7787 | 480 | 28.2138
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 26 | 6.9 | 209.166 |  | 0.277 | 57.939 | 496 | 28.7377
|  | Tinf for setpoint 26 degrees C | [12 empty] | 382.7668
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 27 | 6.1 | 184.9149 |  | 0.277 | 51.2214 | 496 | 25.4058
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 27 | 7 | 212.1974 |  | 0.277 | 58.7787 | 448 | 26.3329
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 27 | 8 | 242.5114 |  | 0.277 | 67.1756 | 496 | 33.3191
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 35.5 | 27 | 8.5 | 257.6683 |  | 0.277 | 71.3741 | 480 | 34.2596
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.7 | 27 | 8.7 | 263.7311 |  | 0.277 | 73.0535 | 496 | 36.2345
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 27 | 7.1 | 215.2288 |  | 0.277 | 59.6184 | 480 | 28.6168
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 27 | 6.2 | 187.9463 |  | 0.277 | 52.0611 | 496 | 25.8223
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 27 | 6.2 | 187.9463 |  | 0.277 | 52.0611 | 496 | 25.8223
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 27 | 6.1 | 184.9149 |  | 0.277 | 51.2214 | 480 | 24.5863
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 27 | 5.9 | 178.8521 |  | 0.277 | 49.542 | 496 | 24.5729
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33 | 27 | 6 | 181.8835 |  | 0.277 | 50.3817 | 480 | 24.1832
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 27 | 5.9 | 178.8521 |  | 0.277 | 49.542 | 496 | 24.5729
|  | Tinf for setpoint 27 degrees C | [12 empty] | 333.7286
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 28 | 5.1 | 154.601 |  | 0.277 | 42.8245 | 496 | 21.2409
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 34 | 28 | 6 | 181.8835 |  | 0.277 | 50.3817 | 448 | 22.571
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 35 | 28 | 7 | 212.1974 |  | 0.277 | 58.7787 | 496 | 29.1542
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 35.5 | 28 | 7.5 | 227.3544 |  | 0.277 | 62.9772 | 480 | 30.229
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 35.7 | 28 | 7.7 | 233.4172 |  | 0.277 | 64.6566 | 496 | 32.0697
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 34.1 | 28 | 6.1 | 184.9149 |  | 0.277 | 51.2214 | 480 | 24.5863
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 28 | 5.2 | 157.6324 |  | 0.277 | 43.6642 | 496 | 21.6574
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 28 | 5.2 | 157.6324 |  | 0.277 | 43.6642 | 496 | 21.6574
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 33.1 | 28 | 5.1 | 154.601 |  | 0.277 | 42.8245 | 480 | 20.5557
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 28 | 4.9 | 148.5382 |  | 0.277 | 41.1451 | 496 | 20.408
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33 | 28 | 5 | 151.5696 |  | 0.277 | 41.9848 | 480 | 20.1527
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.9 | 28 | 4.9 | 148.5382 |  | 0.277 | 41.1451 | 496 | 20.408
|  | Tinf for setpoint 28 degrees C | [12 empty] | 284.6904
Total Internal Load by People
|  | Month | People | SenL/person | CLF | SensL (W) | Latent/Person | LatentL (W) | Total peo L (W) | AC opn hrs |  | Total PL (KWh)
|  | Jan | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Feb | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 448 |  | 188.16
|  | Mar | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Apr | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | May | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Jun | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Jul | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Aug | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Sep | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Oct | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Nov | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Dec | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Total Internal Load by People | [9 empty] | 2452.8
Total Internal Heat Load of Lights per Year
|  | No. Bulbs | Watt Rating | bf | Fu | CLF | hrs (6hrs/day) | Tihlig(KWh)
|  | 3 | 60 | 1.24 | 0.66 | 0.8 | 2190 | 258.0906
|  | Total Internal Heat Load of Lights per Year | [5 empty] | 258.0906
Total Internal Heat Load-Equipment
|  | TV Rating W | Hrs /day | Total hrs | Tihe (KWh)
|  | 36 | 5 | 1825 | 65.7
|  | Total load Equipment |  |  | 65.7
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 22 | 154.132 | 267.4925 | 578.9197 | 2452.8 | 258.0906 | 65.7 | 3777.1348
|  | 23 | 125.7496 | 267.4925 | 529.8815 | 2452.8 | 258.0906 | 65.7 | 3699.7142
|  | 24 | 97.3672 | 267.4925 | 480.8433 | 2452.8 | 258.0906 | 65.7 | 3622.2936
|  | 25 | 68.9848 | 267.4925 | 431.8051 | 2452.8 | 258.0906 | 65.7 | 3544.873
|  | 26 | 40.6024 | 267.4925 | 382.7668 | 2452.8 | 258.0906 | 65.7 | 3467.4523
|  | 27 | 12.22 | 267.4925 | 333.7286 | 2452.8 | 258.0906 | 65.7 | 3390.0317
|  | 28 | -16.1624 | 267.4925 | 284.6904 | 2452.8 | 258.0906 | 65.7 | 3312.6111

## All Season Dengue Endemic_PH
Balance Point Temperature, Annual Variable Degree Days, Thermal Load of Living Space and Annual Electricity Consumption Calculations for Chennai- Baseline and Solar Electricity Scenarios
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | AC hrs/24 hrs (fAC) | Conv (24/1000) KWh |  |  | Annual VCDD |  |  |  | Annual VCDD |  |  |  | Annual VCDD |  | All Other Heat Loads | BE+Other Loads | 10%SF |  | EER | Elec. Cons.
|  | Jan | 22 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9605 | 19 | 236.1 | [23 empty] | LDRZ Setpoint Adjsuted Preference %
|  | Feb | 22 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9434 | 19 | 218.8 | [23 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Mar | 22 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9319 | 19 | 279.5 | [23 empty] | 22 | 16 | 0.34783
|  | Apr | 22 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.909 | 19 | 321.1 | [23 empty] | 23 | 10 | 0.21739
|  | May | 22 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8347 | 19 | 350.7 | [23 empty] | 24 | 20 | 0.43478
|  | Jun | 22 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.7545 | 19 | 312.1 | [24 empty] | 46
|  | July | 22 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8175 | 19 | 289.6
|  | Aug | 22 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8976 | 19 | 302.8
|  | Sep | 22 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9262 | 19 | 268.1
|  | Oct | 22 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9434 | 19 | 272.4
|  | Nov | 22 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9605 | 19 | 270.1
|  | Dec | 22 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9662 | 19 | 244.4
|  | Annual VCDD | [9 empty] | 3365.7 | 0.66667 | 0.024 | 3.59 | 12.96 | 3365.7 | 2505.5025 | 3.94 | 12.96 | 3365.7 | 2749.7715 | 2.13 | 41.904 | 3365.7 | 4806.5169 | 3633.9464 | 13695.7372 | 1369.5737 | 15065.3109 | 3.1 | 4860 | 22
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 23 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9605 | 20 | 205.1
|  | Feb | 23 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9434 | 20 | 190.8
|  | Mar | 23 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9319 | 20 | 248.5
|  | Apr | 23 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.909 | 20 | 291.1
|  | May | 23 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8347 | 20 | 319.7
|  | Jun | 23 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.7545 | 20 | 282.1
|  | July | 23 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8175 | 20 | 258.6
|  | Aug | 23 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8976 | 20 | 271.8
|  | Sep | 23 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9262 | 20 | 238.1
|  | Oct | 23 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9434 | 20 | 241.4
|  | Nov | 23 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9605 | 20 | 240.1
|  | Dec | 23 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9662 | 20 | 213.4
|  | Annual VCDD | [9 empty] | 3000.7 | 0.66667 | 0.024 | 3.59 | 12.96 | 3000.7 | 2233.7883 | 3.94 | 12.96 | 3000.7 | 2451.5671 | 2.13 | 41.904 | 3000.7 | 4285.2646 | 3556.5257 | 12527.1457 | 1252.7146 | 13779.8603 | 3.1 | 4445 | 23
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 24 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9605 | 21 | 174.1
|  | Feb | 24 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9434 | 21 | 162.8
|  | Mar | 24 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9319 | 21 | 217.5
|  | Apr | 24 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.909 | 21 | 261.1
|  | May | 24 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8347 | 21 | 288.7
|  | Jun | 24 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.7545 | 21 | 252.1
|  | Jul | 24 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8175 | 21 | 227.6
|  | Aug | 24 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8976 | 21 | 240.8
|  | Sep | 24 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9262 | 21 | 208.1
|  | Oct | 24 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9434 | 21 | 210.4
|  | Nov | 24 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9605 | 21 | 210.1
|  | Dec | 24 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9662 | 21 | 182.4
|  | Annual VCDD | [9 empty] | 2635.7 | 0.66667 | 0.024 | 3.59 | 12.96 | 2635.7 | 1962.0741 | 3.94 | 12.96 | 2635.7 | 2153.3627 | 2.13 | 41.904 | 2635.7 | 3764.0124 | 3479.1051 | 11358.5543 | 1135.8554 | 12494.4097 | 3.1 | 4030 | 24
|  | Avg Energy Consumption of AC UnIt for LDRZ | [29 empty] | 4408.913
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | [23 empty] | MDRZ Setpoint Adjsuted Preference %
|  | Jan | 25 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9605 | 22 | 143.3 | [23 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Feb | 25 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9434 | 22 | 134.9 | [23 empty] | 25 | 12 | 100
|  | Mar | 25 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9319 | 22 | 186.6
|  | Apr | 25 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.909 | 22 | 231.1
|  | May | 25 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8347 | 22 | 257.7
|  | Jun | 25 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.7545 | 22 | 222.1 | [22 empty] | 792.913
|  | Jul | 25 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8175 | 22 | 196.6
|  | Aug | 25 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8976 | 22 | 209.8
|  | Sep | 25 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9262 | 22 | 178.1
|  | Oct | 25 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9434 | 22 | 179.4
|  | Nov | 25 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9605 | 22 | 180.1
|  | Dec | 25 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9662 | 22 | 151.4
|  | Annual VCDD | [9 empty] | 2271.1 | 0.66667 | 0.024 | 3.59 | 12.96 | 2271.1 | 1690.6577 | 3.94 | 12.96 | 2271.1 | 1855.4851 | 2.13 | 41.904 | 2271.1 | 3243.3314 | 3401.6845 | 10191.1587 | 1019.1159 | 11210.2745 | 3.1 | 3616 | 25
|  | Avg Energy Consumption of AC Unit for MDRZ | [29 empty] | 3616
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 26 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9605 | 23 | 113.1
|  | Feb | 26 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9434 | 23 | 107.2
|  | Mar | 26 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9319 | 23 | 156.3
|  | Apr | 26 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.909 | 23 | 201.1
|  | May | 26 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8347 | 23 | 226.7
|  | Jun | 26 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.7545 | 23 | 192.1
|  | July | 26 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8175 | 23 | 165.6
|  | Aug | 26 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8976 | 23 | 178.8
|  | Sep | 26 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9262 | 23 | 148.1
|  | Oct | 26 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9434 | 23 | 148.4
|  | Nov | 26 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9605 | 23 | 150.1
|  | Dec | 26 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9662 | 23 | 120.4
|  | Annual VCDD | [9 empty] | 1907.9 | 0.66667 | 0.024 | 3.59 | 12.96 | 1907.9 | 1420.2835 | 3.94 | 12.96 | 1907.9 | 1558.7512 | 2.13 | 41.904 | 1907.9 | 2724.6497 | 3324.2639 | 9027.9483 | 902.7948 | 9930.7431 | 3.1 | 3203 | 26
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 27 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9605 | 24 | 84.8 | [23 empty] | HDRZ Setpoint Adjsuted Preference %
|  | Feb | 27 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9434 | 24 | 80.5 | [23 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Mar | 27 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9319 | 24 | 126.5 | [23 empty] | 26 | 10 | 0.5
|  | Apr | 27 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.909 | 24 | 171.2 | [23 empty] | 27 | 8 | 0.4
|  | May | 27 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8347 | 24 | 195.7 | [23 empty] | 28 | 2 | 0.1
|  | Jun | 27 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.7545 | 24 | 162.1 | [24 empty] | 20
|  | Jul | 27 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8175 | 24 | 134.6
|  | Aug | 27 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8976 | 24 | 147.8
|  | Sep | 27 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9262 | 24 | 118.1
|  | Oct | 27 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9434 | 24 | 117.4
|  | Nov | 27 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9605 | 24 | 120.8
|  | Dec | 27 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9662 | 24 | 89.5
|  | Annual VCDD | [9 empty] | 1549 | 0.66667 | 0.024 | 3.59 | 12.96 | 1549 | 1153.1103 | 3.94 | 12.96 | 1549 | 1265.5305 | 2.13 | 41.904 | 1549 | 2212.1088 | 3246.8432 | 7877.5929 | 787.7593 | 8665.3522 | 3.1 | 2795 | 27
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 28 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9605 | 25 | 60.2
|  | Feb | 28 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9434 | 25 | 57.5
|  | Mar | 28 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9319 | 25 | 98.4
|  | Apr | 28 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.909 | 25 | 142.1
|  | May | 28 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8347 | 25 | 164.7
|  | Jun | 28 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.7545 | 25 | 132.1
|  | Jul | 28 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8175 | 25 | 103.7
|  | Aug | 28 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8976 | 25 | 116.8
|  | Sep | 28 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9262 | 25 | 88.1
|  | Oct | 28 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9434 | 25 | 86.9
|  | Nov | 28 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9605 | 25 | 93.1
|  | Dec | 28 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9662 | 25 | 61.2
|  | Annual VCDD | [9 empty] | 1204.8 | 0.66667 | 0.024 | 3.59 | 12.96 | 1204.8 | 896.8801 | 3.94 | 12.96 | 1204.8 | 984.3197 | 2.13 | 41.904 | 1204.8 | 1720.5608 | 3169.4226 | 6771.1832 | 677.1183 | 7448.3015 | 3.1 | 2403 | 28
|  | Avg Energy Consumption of AC Unit for HDRZ | [29 empty] | 2960 |  | 1448.913
CLTDgw-avg (°C) for AC Opn hrs. |  | Thermal Conductive Load (TLgw-x) Calculated for Three Climate Zones
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 22°C
AC Opn hrs. | CLTDgw (°C) | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
00.00-01.00 | 1 | Jan | 29.1 | 2.9 | 1.45 | 27.65 | 1.75 | 22 | 3.5 | -1.75 | 3.5 | 3.75 | 1.296 | 496 | 8.437
01.00-02.00 | 1 | Feb | 29.5 | 3.3 | 1.65 | 27.85 | 1.75 | 22 | 3.5 | -1.55 | 3.7 | 3.75 | 1.296 | 448 | 8.0559
02.00-03.00 | 0 | Mar | 30.6 | 3.8 | 1.9 | 28.7 | 1.75 | 22 | 3.5 | -0.7 | 4.55 | 3.75 | 1.296 | 496 | 10.968
03.00-04.00 | -1 | Apr | 31.3 | 4.1 | 2.05 | 29.25 | 1.75 | 22 | 3.5 | -0.15 | 5.1 | 3.75 | 1.296 | 480 | 11.8973
04.00-05.00 | -1 | May | 32.7 | 4.8 | 2.4 | 30.3 | 1.75 | 22 | 3.5 | 0.9 | 6.15 | 3.75 | 1.296 | 496 | 14.8249
05.00-06.00 | -1 | Jun | 32.6 | 4.8 | 2.4 | 30.2 | 1.75 | 22 | 3.5 | 0.8 | 6.05 | 3.75 | 1.296 | 480 | 14.1134
06.00-07.00 | -1 | Jul | 31.7 | 4.6 | 2.3 | 29.4 | 1.75 | 22 | 3.5 | 0 | 5.25 | 3.75 | 1.296 | 496 | 12.6554
07.00-08.00 | -1 | Aug | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 22 | 3.5 | 0.4 | 5.65 | 3.75 | 1.296 | 496 | 13.6197
08.00-09.00 | 0 | Sep | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 22 | 3.5 | 0.4 | 5.65 | 3.75 | 1.296 | 480 | 13.1803
17.00-18.00 | 7 | Oct | 31.6 | 4.4 | 2.2 | 29.4 | 1.75 | 22 | 3.5 | 0 | 5.25 | 3.75 | 1.296 | 496 | 12.6554
18.00-19.00 | 7 | Nov | 30.6 | 3.7 | 1.85 | 28.75 | 1.75 | 22 | 3.5 | -0.65 | 4.6 | 3.75 | 1.296 | 480 | 10.7309
19.00-20.00 | 6 | Dec | 29.7 | 3.1 | 1.55 | 28.15 | 1.75 | 22 | 3.5 | -1.25 | 4 | 3.75 | 1.296 | 496 | 9.6422
20.00-21.00 | 4 | TLgw-CHN (KWh) | [12 empty] | 140.7806
21.00-22.00 | 3 | Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 23°C
22.00-23.00 | 2 | Jan | 29.1 | 2.9 | 1.45 | 27.65 | 1.75 | 23 | 2.5 | -1.75 | 2.5 | 3.75 | 1.296 | 496 | 6.0264
23.00-00.00 | 2 | Feb | 29.5 | 3.3 | 1.65 | 27.85 | 1.75 | 23 | 2.5 | -1.55 | 2.7 | 3.75 | 1.296 | 448 | 5.8787
CLTDgw-avg (°C) | 1.75 | Mar | 30.6 | 3.8 | 1.9 | 28.7 | 1.75 | 23 | 2.5 | -0.7 | 3.55 | 3.75 | 1.296 | 496 | 8.5575
|  | Apr | 31.3 | 4.1 | 2.05 | 29.25 | 1.75 | 23 | 2.5 | -0.15 | 4.1 | 3.75 | 1.296 | 480 | 9.5645
|  | May | 32.7 | 4.8 | 2.4 | 30.3 | 1.75 | 23 | 2.5 | 0.9 | 5.15 | 3.75 | 1.296 | 496 | 12.4144
|  | Jun | 32.6 | 4.8 | 2.4 | 30.2 | 1.75 | 23 | 2.5 | 0.8 | 5.05 | 3.75 | 1.296 | 480 | 11.7806
|  | Jul | 31.7 | 4.6 | 2.3 | 29.4 | 1.75 | 23 | 2.5 | 0 | 4.25 | 3.75 | 1.296 | 496 | 10.2449
|  | Aug | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 23 | 2.5 | 0.4 | 4.65 | 3.75 | 1.296 | 496 | 11.2091
|  | Sep | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 23 | 2.5 | 0.4 | 4.65 | 3.75 | 1.296 | 480 | 10.8475
|  | Oct | 31.6 | 4.4 | 2.2 | 29.4 | 1.75 | 23 | 2.5 | 0 | 4.25 | 3.75 | 1.296 | 496 | 10.2449
|  | Nov | 30.6 | 3.7 | 1.85 | 28.75 | 1.75 | 23 | 2.5 | -0.65 | 3.6 | 3.75 | 1.296 | 480 | 8.3981
|  | Dec | 29.7 | 3.1 | 1.55 | 28.15 | 1.75 | 23 | 2.5 | -1.25 | 3 | 3.75 | 1.296 | 496 | 7.2317
|  | TLgw-CHN (KWh) | [12 empty] | 112.3982
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 24°C
|  | Jan | 29.1 | 2.9 | 1.45 | 27.65 | 1.75 | 24 | 1.5 | -1.75 | 1.5 | 3.75 | 1.296 | 496 | 3.6158
|  | Feb | 29.5 | 3.3 | 1.65 | 27.85 | 1.75 | 24 | 1.5 | -1.55 | 1.7 | 3.75 | 1.296 | 448 | 3.7014
|  | Mar | 30.6 | 3.8 | 1.9 | 28.7 | 1.75 | 24 | 1.5 | -0.7 | 2.55 | 3.75 | 1.296 | 496 | 6.1469
|  | Apr | 31.3 | 4.1 | 2.05 | 29.25 | 1.75 | 24 | 1.5 | -0.15 | 3.1 | 3.75 | 1.296 | 480 | 7.2317
|  | May | 32.7 | 4.8 | 2.4 | 30.3 | 1.75 | 24 | 1.5 | 0.9 | 4.15 | 3.75 | 1.296 | 496 | 10.0038
|  | Jun | 32.6 | 4.8 | 2.4 | 30.2 | 1.75 | 24 | 1.5 | 0.8 | 4.05 | 3.75 | 1.296 | 480 | 9.4478
|  | Jul | 31.7 | 4.6 | 2.3 | 29.4 | 1.75 | 24 | 1.5 | 0 | 3.25 | 3.75 | 1.296 | 496 | 7.8343
|  | Aug | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 24 | 1.5 | 0.4 | 3.65 | 3.75 | 1.296 | 496 | 8.7985
|  | Sep | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 24 | 1.5 | 0.4 | 3.65 | 3.75 | 1.296 | 480 | 8.5147
|  | Oct | 31.6 | 4.4 | 2.2 | 29.4 | 1.75 | 24 | 1.5 | 0 | 3.25 | 3.75 | 1.296 | 496 | 7.8343
|  | Nov | 30.6 | 3.7 | 1.85 | 28.75 | 1.75 | 24 | 1.5 | -0.65 | 2.6 | 3.75 | 1.296 | 480 | 6.0653
|  | Dec | 29.7 | 3.1 | 1.55 | 28.15 | 1.75 | 24 | 1.5 | -1.25 | 2 | 3.75 | 1.296 | 496 | 4.8211
|  | TLgw-AMD (KWh) | [12 empty] | 84.0158
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 25°C
|  | Jan | 29.1 | 2.9 | 1.45 | 27.65 | 1.75 | 25 | 0.5 | -1.75 | 0.5 | 3.75 | 1.296 | 496 | 1.2053
|  | Feb | 29.5 | 3.3 | 1.65 | 27.85 | 1.75 | 25 | 0.5 | -1.55 | 0.7 | 3.75 | 1.296 | 448 | 1.5241
|  | Mar | 30.6 | 3.8 | 1.9 | 28.7 | 1.75 | 25 | 0.5 | -0.7 | 1.55 | 3.75 | 1.296 | 496 | 3.7364
|  | Apr | 31.3 | 4.1 | 2.05 | 29.25 | 1.75 | 25 | 0.5 | -0.15 | 2.1 | 3.75 | 1.296 | 480 | 4.8989
|  | May | 32.7 | 4.8 | 2.4 | 30.3 | 1.75 | 25 | 0.5 | 0.9 | 3.15 | 3.75 | 1.296 | 496 | 7.5933
|  | Jun | 32.6 | 4.8 | 2.4 | 30.2 | 1.75 | 25 | 0.5 | 0.8 | 3.05 | 3.75 | 1.296 | 480 | 7.115
|  | Jul | 31.7 | 4.6 | 2.3 | 29.4 | 1.75 | 25 | 0.5 | 0 | 2.25 | 3.75 | 1.296 | 496 | 5.4238
|  | Aug | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 25 | 0.5 | 0.4 | 2.65 | 3.75 | 1.296 | 496 | 6.388
|  | Sep | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 25 | 0.5 | 0.4 | 2.65 | 3.75 | 1.296 | 480 | 6.1819
|  | Oct | 31.6 | 4.4 | 2.2 | 29.4 | 1.75 | 25 | 0.5 | 0 | 2.25 | 3.75 | 1.296 | 496 | 5.4238
|  | Nov | 30.6 | 3.7 | 1.85 | 28.75 | 1.75 | 25 | 0.5 | -0.65 | 1.6 | 3.75 | 1.296 | 480 | 3.7325
|  | Dec | 29.7 | 3.1 | 1.55 | 28.15 | 1.75 | 25 | 0.5 | -1.25 | 1 | 3.75 | 1.296 | 496 | 2.4106
|  | TLgw-DEL (KWh) | [12 empty] | 55.6334
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 26°C
|  | Jan | 29.1 | 2.9 | 1.45 | 27.65 | 1.75 | 26 | -0.5 | -1.75 | -0.5 | 3.75 | 1.296 | 496 | -1.2053
|  | Feb | 29.5 | 3.3 | 1.65 | 27.85 | 1.75 | 26 | -0.5 | -1.55 | -0.3 | 3.75 | 1.296 | 448 | -0.65318
|  | Mar | 30.6 | 3.8 | 1.9 | 28.7 | 1.75 | 26 | -0.5 | -0.7 | 0.55 | 3.75 | 1.296 | 496 | 1.3258
|  | Apr | 31.3 | 4.1 | 2.05 | 29.25 | 1.75 | 26 | -0.5 | -0.15 | 1.1 | 3.75 | 1.296 | 480 | 2.5661
|  | May | 32.7 | 4.8 | 2.4 | 30.3 | 1.75 | 26 | -0.5 | 0.9 | 2.15 | 3.75 | 1.296 | 496 | 5.1827
|  | Jun | 32.6 | 4.8 | 2.4 | 30.2 | 1.75 | 26 | -0.5 | 0.8 | 2.05 | 3.75 | 1.296 | 480 | 4.7822
|  | Jul | 31.7 | 4.6 | 2.3 | 29.4 | 1.75 | 26 | -0.5 | 0 | 1.25 | 3.75 | 1.296 | 496 | 3.0132
|  | Aug | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 26 | -0.5 | 0.4 | 1.65 | 3.75 | 1.296 | 496 | 3.9774
|  | Sep | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 26 | -0.5 | 0.4 | 1.65 | 3.75 | 1.296 | 480 | 3.8491
|  | Oct | 31.6 | 4.4 | 2.2 | 29.4 | 1.75 | 26 | -0.5 | 0 | 1.25 | 3.75 | 1.296 | 496 | 3.0132
|  | Nov | 30.6 | 3.7 | 1.85 | 28.75 | 1.75 | 26 | -0.5 | -0.65 | 0.6 | 3.75 | 1.296 | 480 | 1.3997
|  | Dec | 29.7 | 3.1 | 1.55 | 28.15 | 1.75 | 26 | -0.5 | -1.25 | 0 | 3.75 | 1.296 | 496 | 0
|  | TLgw-DEL (KWh) | [12 empty] | 27.251
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 27°C
|  | Jan | 29.1 | 2.9 | 1.45 | 27.65 | 1.75 | 27 | -1.5 | -1.75 | -1.5 | 3.75 | 1.296 | 496 | -3.6158
|  | Feb | 29.5 | 3.3 | 1.65 | 27.85 | 1.75 | 27 | -1.5 | -1.55 | -1.3 | 3.75 | 1.296 | 448 | -2.8305
|  | Mar | 30.6 | 3.8 | 1.9 | 28.7 | 1.75 | 27 | -1.5 | -0.7 | -0.45 | 3.75 | 1.296 | 496 | -1.0848
|  | Apr | 31.3 | 4.1 | 2.05 | 29.25 | 1.75 | 27 | -1.5 | -0.15 | 0.1 | 3.75 | 1.296 | 480 | 0.23328
|  | May | 32.7 | 4.8 | 2.4 | 30.3 | 1.75 | 27 | -1.5 | 0.9 | 1.15 | 3.75 | 1.296 | 496 | 2.7721
|  | Jun | 32.6 | 4.8 | 2.4 | 30.2 | 1.75 | 27 | -1.5 | 0.8 | 1.05 | 3.75 | 1.296 | 480 | 2.4494
|  | Jul | 31.7 | 4.6 | 2.3 | 29.4 | 1.75 | 27 | -1.5 | 0 | 0.25 | 3.75 | 1.296 | 496 | 0.60264
|  | Aug | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 27 | -1.5 | 0.4 | 0.65 | 3.75 | 1.296 | 496 | 1.5669
|  | Sep | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 27 | -1.5 | 0.4 | 0.65 | 3.75 | 1.296 | 480 | 1.5163
|  | Oct | 31.6 | 4.4 | 2.2 | 29.4 | 1.75 | 27 | -1.5 | 0 | 0.25 | 3.75 | 1.296 | 496 | 0.60264
|  | Nov | 30.6 | 3.7 | 1.85 | 28.75 | 1.75 | 27 | -1.5 | -0.65 | -0.4 | 3.75 | 1.296 | 480 | -0.93312
|  | Dec | 29.7 | 3.1 | 1.55 | 28.15 | 1.75 | 27 | -1.5 | -1.25 | -1 | 3.75 | 1.296 | 496 | -2.4106
|  | TLgw-DEL (KWh) | [12 empty] | -1.1314
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 28°C
|  | Jan | 29.1 | 2.9 | 1.45 | 27.65 | 1.75 | 28 | -2.5 | -1.75 | -2.5 | 3.75 | 1.296 | 496 | -6.0264
|  | Feb | 29.5 | 3.3 | 1.65 | 27.85 | 1.75 | 28 | -2.5 | -1.55 | -2.3 | 3.75 | 1.296 | 448 | -5.0077
|  | Mar | 30.6 | 3.8 | 1.9 | 28.7 | 1.75 | 28 | -2.5 | -0.7 | -1.45 | 3.75 | 1.296 | 496 | -3.4953
|  | Apr | 31.3 | 4.1 | 2.05 | 29.25 | 1.75 | 28 | -2.5 | -0.15 | -0.9 | 3.75 | 1.296 | 480 | -2.0995
|  | May | 32.7 | 4.8 | 2.4 | 30.3 | 1.75 | 28 | -2.5 | 0.9 | 0.15 | 3.75 | 1.296 | 496 | 0.36158
|  | Jun | 32.6 | 4.8 | 2.4 | 30.2 | 1.75 | 28 | -2.5 | 0.8 | 0.05 | 3.75 | 1.296 | 480 | 0.11664
|  | Jul | 31.7 | 4.6 | 2.3 | 29.4 | 1.75 | 28 | -2.5 | 0 | -0.75 | 3.75 | 1.296 | 496 | -1.8079
|  | Aug | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 28 | -2.5 | 0.4 | -0.35 | 3.75 | 1.296 | 496 | -0.8437
|  | Sep | 32.2 | 4.8 | 2.4 | 29.8 | 1.75 | 28 | -2.5 | 0.4 | -0.35 | 3.75 | 1.296 | 480 | -0.81648
|  | Oct | 31.6 | 4.4 | 2.2 | 29.4 | 1.75 | 28 | -2.5 | 0 | -0.75 | 3.75 | 1.296 | 496 | -1.8079
|  | Nov | 30.6 | 3.7 | 1.85 | 28.75 | 1.75 | 28 | -2.5 | -0.65 | -1.4 | 3.75 | 1.296 | 480 | -3.2659
|  | Dec | 29.7 | 3.1 | 1.55 | 28.15 | 1.75 | 28 | -2.5 | -1.25 | -2 | 3.75 | 1.296 | 496 | -4.8211
|  | TLgw-DEL (KWh) | [12 empty] | -29.5138
Annual Radiation Thermal Load Through Glass Window
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jan | 0.55 | 0.51 | 94.63 | 1.296 | 496 | 17.0627
|  | Feb | 0.55 | 0.51 | 104.1 | 1.296 | 448 | 16.9538
|  | Mar | 0.55 | 0.51 | 110.41 | 1.296 | 496 | 19.908
|  | Apr | 0.55 | 0.51 | 123.02 | 1.296 | 480 | 21.4662
|  | May | 0.55 | 0.51 | 164.03 | 1.296 | 496 | 29.5762
|  | Jun | 0.55 | 0.51 | 208.2 | 1.296 | 480 | 36.3295
|  | Jul | 0.55 | 0.51 | 173.5 | 1.296 | 496 | 31.2838
|  | Aug | 0.55 | 0.51 | 129.33 | 1.296 | 496 | 23.3195
|  | Sep | 0.55 | 0.51 | 113.56 | 1.296 | 480 | 19.8155
|  | Oct | 0.55 | 0.51 | 104.1 | 1.296 | 496 | 18.7703
|  | Nov | 0.55 | 0.51 | 94.63 | 1.296 | 480 | 16.5123
|  | Dec | 0.55 | 0.51 | 91.48 | 1.296 | 496 | 16.4947
|  | TLrad | [5 empty] | 267.4925
Inflitration Load for Different Setpoint Temperatures
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) |  | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 29.1 | 22 | 7.1 | 215.2288 |  | 0.277 | 59.6184 | 496 | 29.5707
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 29.5 | 22 | 7.5 | 227.3544 |  | 0.277 | 62.9772 | 448 | 28.2138
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 22 | 8.6 | 260.6997 |  | 0.277 | 72.2138 | 496 | 35.8181
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 31.3 | 22 | 9.3 | 281.9195 |  | 0.277 | 78.0917 | 480 | 37.484
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.7 | 22 | 10.7 | 324.3589 |  | 0.277 | 89.8474 | 496 | 44.5643
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.6 | 22 | 10.6 | 321.3275 |  | 0.277 | 89.0077 | 480 | 42.7237
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 22 | 9.7 | 294.045 |  | 0.277 | 81.4505 | 496 | 40.3994
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 22 | 10.2 | 309.202 |  | 0.277 | 85.6489 | 496 | 42.4819
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 22 | 10.2 | 309.202 |  | 0.277 | 85.6489 | 480 | 41.1115
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 22 | 9.6 | 291.0136 |  | 0.277 | 80.6108 | 496 | 39.9829
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 22 | 8.6 | 260.6997 |  | 0.277 | 72.2138 | 480 | 34.6626
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 29.7 | 22 | 7.7 | 233.4172 |  | 0.277 | 64.6566 | 496 | 32.0697
|  | Tinf for setpoint 22 degrees C | [12 empty] | 449.0826
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 29.1 | 23 | 6.1 | 184.9149 |  | 0.277 | 51.2214 | 496 | 25.4058
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 29.5 | 23 | 6.5 | 197.0405 |  | 0.277 | 54.5802 | 448 | 24.4519
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 23 | 7.6 | 230.3858 |  | 0.277 | 63.8169 | 496 | 31.6532
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 31.3 | 23 | 8.3 | 251.6055 |  | 0.277 | 69.6947 | 480 | 33.4535
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.7 | 23 | 9.7 | 294.045 |  | 0.277 | 81.4505 | 496 | 40.3994
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.6 | 23 | 9.6 | 291.0136 |  | 0.277 | 80.6108 | 480 | 38.6932
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 23 | 8.7 | 263.7311 |  | 0.277 | 73.0535 | 496 | 36.2345
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 23 | 9.2 | 278.8881 |  | 0.277 | 77.252 | 496 | 38.317
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 23 | 9.2 | 278.8881 |  | 0.277 | 77.252 | 480 | 37.081
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 23 | 8.6 | 260.6997 |  | 0.277 | 72.2138 | 496 | 35.8181
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 23 | 7.6 | 230.3858 |  | 0.277 | 63.8169 | 480 | 30.6321
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 29.7 | 23 | 6.7 | 203.1033 |  | 0.277 | 56.2596 | 496 | 27.9048
|  | Tinf for setpoint 23 degrees C | [12 empty] | 400.0444
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 29.1 | 24 | 5.1 | 154.601 |  | 0.277 | 42.8245 | 496 | 21.2409
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 29.5 | 24 | 5.5 | 166.7266 |  | 0.277 | 46.1833 | 448 | 20.6901
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 24 | 6.6 | 200.0719 |  | 0.277 | 55.4199 | 496 | 27.4883
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 31.3 | 24 | 7.3 | 221.2916 |  | 0.277 | 61.2978 | 480 | 29.4229
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.7 | 24 | 8.7 | 263.7311 |  | 0.277 | 73.0535 | 496 | 36.2345
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.6 | 24 | 8.6 | 260.6997 |  | 0.277 | 72.2138 | 480 | 34.6626
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 24 | 7.7 | 233.4172 |  | 0.277 | 64.6566 | 496 | 32.0697
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 24 | 8.2 | 248.5741 |  | 0.277 | 68.855 | 496 | 34.1521
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 24 | 8.2 | 248.5741 |  | 0.277 | 68.855 | 480 | 33.0504
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 24 | 7.6 | 230.3858 |  | 0.277 | 63.8169 | 496 | 31.6532
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 24 | 6.6 | 200.0719 |  | 0.277 | 55.4199 | 480 | 26.6016
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 29.7 | 24 | 5.7 | 172.7893 |  | 0.277 | 47.8626 | 496 | 23.7399
|  | Tinf for setpoint 24 degrees C | [12 empty] | 351.0062
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 29.1 | 25 | 4.1 | 124.2871 |  | 0.277 | 34.4275 | 496 | 17.076
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 29.5 | 25 | 4.5 | 136.4126 |  | 0.277 | 37.7863 | 448 | 16.9283
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 25 | 5.6 | 169.7579 |  | 0.277 | 47.023 | 496 | 23.3234
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 31.3 | 25 | 6.3 | 190.9777 |  | 0.277 | 52.9008 | 480 | 25.3924
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.7 | 25 | 7.7 | 233.4172 |  | 0.277 | 64.6566 | 496 | 32.0697
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.6 | 25 | 7.6 | 230.3858 |  | 0.277 | 63.8169 | 480 | 30.6321
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 25 | 6.7 | 203.1033 |  | 0.277 | 56.2596 | 496 | 27.9048
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 25 | 7.2 | 218.2602 |  | 0.277 | 60.4581 | 496 | 29.9872
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 25 | 7.2 | 218.2602 |  | 0.277 | 60.4581 | 480 | 29.0199
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 25 | 6.6 | 200.0719 |  | 0.277 | 55.4199 | 496 | 27.4883
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 25 | 5.6 | 169.7579 |  | 0.277 | 47.023 | 480 | 22.571
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 29.7 | 25 | 4.7 | 142.4754 |  | 0.277 | 39.4657 | 496 | 19.575
|  | Tinf for setpoint 25 degrees C | [12 empty] | 301.968
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 29.1 | 26 | 3.1 | 93.9732 |  | 0.277 | 26.0306 | 496 | 12.9112
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 29.5 | 26 | 3.5 | 106.0987 |  | 0.277 | 29.3893 | 448 | 13.1664
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 26 | 4.6 | 139.444 |  | 0.277 | 38.626 | 496 | 19.1585
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 31.3 | 26 | 5.3 | 160.6638 |  | 0.277 | 44.5039 | 480 | 21.3619
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.7 | 26 | 6.7 | 203.1033 |  | 0.277 | 56.2596 | 496 | 27.9048
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.6 | 26 | 6.6 | 200.0719 |  | 0.277 | 55.4199 | 480 | 26.6016
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 26 | 5.7 | 172.7893 |  | 0.277 | 47.8626 | 496 | 23.7399
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 26 | 6.2 | 187.9463 |  | 0.277 | 52.0611 | 496 | 25.8223
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 26 | 6.2 | 187.9463 |  | 0.277 | 52.0611 | 480 | 24.9893
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 26 | 5.6 | 169.7579 |  | 0.277 | 47.023 | 496 | 23.3234
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 26 | 4.6 | 139.444 |  | 0.277 | 38.626 | 480 | 18.5405
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 29.7 | 26 | 3.7 | 112.1615 |  | 0.277 | 31.0687 | 496 | 15.4101
|  | Tinf for setpoint 26 degrees C | [12 empty] | 252.9297
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 29.1 | 27 | 2.1 | 63.6592 |  | 0.277 | 17.6336 | 496 | 8.7463
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 29.5 | 27 | 2.5 | 75.7848 |  | 0.277 | 20.9924 | 448 | 9.4046
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 27 | 3.6 | 109.1301 |  | 0.277 | 30.229 | 496 | 14.9936
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 31.3 | 27 | 4.3 | 130.3499 |  | 0.277 | 36.1069 | 480 | 17.3313
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.7 | 27 | 5.7 | 172.7893 |  | 0.277 | 47.8626 | 496 | 23.7399
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.6 | 27 | 5.6 | 169.7579 |  | 0.277 | 47.023 | 480 | 22.571
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 27 | 4.7 | 142.4754 |  | 0.277 | 39.4657 | 496 | 19.575
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 27 | 5.2 | 157.6324 |  | 0.277 | 43.6642 | 496 | 21.6574
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 27 | 5.2 | 157.6324 |  | 0.277 | 43.6642 | 480 | 20.9588
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 27 | 4.6 | 139.444 |  | 0.277 | 38.626 | 496 | 19.1585
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 27 | 3.6 | 109.1301 |  | 0.277 | 30.229 | 480 | 14.5099
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 29.7 | 27 | 2.7 | 81.8476 |  | 0.277 | 22.6718 | 496 | 11.2452
|  | Tinf for setpoint 27 degrees C | [12 empty] | 203.8915
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 29.1 | 28 | 1.1 | 33.3453 |  | 0.277 | 9.2367 | 496 | 4.5814
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 29.5 | 28 | 1.5 | 45.4709 |  | 0.277 | 12.5954 | 448 | 5.6428
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 28 | 2.6 | 78.8162 |  | 0.277 | 21.8321 | 496 | 10.8287
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 31.3 | 28 | 3.3 | 100.0359 |  | 0.277 | 27.71 | 480 | 13.3008
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.7 | 28 | 4.7 | 142.4754 |  | 0.277 | 39.4657 | 496 | 19.575
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.6 | 28 | 4.6 | 139.444 |  | 0.277 | 38.626 | 480 | 18.5405
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 28 | 3.7 | 112.1615 |  | 0.277 | 31.0687 | 496 | 15.4101
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 28 | 4.2 | 127.3185 |  | 0.277 | 35.2672 | 496 | 17.4925
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 28 | 4.2 | 127.3185 |  | 0.277 | 35.2672 | 480 | 16.9283
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 28 | 3.6 | 109.1301 |  | 0.277 | 30.229 | 496 | 14.9936
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 30.6 | 28 | 2.6 | 78.8162 |  | 0.277 | 21.8321 | 480 | 10.4794
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 29.7 | 28 | 1.7 | 51.5337 |  | 0.277 | 14.2748 | 496 | 7.0803
|  | Tinf for setpoint 28 degrees C | [12 empty] | 154.8533
Total Internal Load by People
|  | Month | People | SenL/person | CLF | SensL (W) | Latent/Person | LatentL (W) | Total peo L (W) | AC opn hrs |  | Total PL (KWh)
|  | Jan | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Feb | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 448 |  | 188.16
|  | Mar | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Apr | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | May | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Jun | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Jul | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Aug | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Sep | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Oct | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Nov | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Dec | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Total Internal Load by People | [9 empty] | 2452.8
Total Internal Heat Load of Lights per Year
|  | No. Bulbs | Watt Rating | bf | Fu | CLF | hrs (6hrs/day) | Tihlig(KWh)
|  | 3 | 60 | 1.24 | 0.66 | 0.8 | 2190 | 258.0906
|  | Total Internal Heat Load of Lights per Year | [5 empty] | 258.0906
Total Internal Heat Load-Equipment
|  | TV Rating W | Hrs /day | Total hrs | Tihe (KWh)
|  | 36 | 5 | 1825 | 65.7
|  | Total load Equipment |  |  | 65.7
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 22 | 140.7806 | 267.4925 | 449.0826 | 2452.8 | 258.0906 | 65.7 | 3633.9464
|  | 23 | 112.3982 | 267.4925 | 400.0444 | 2452.8 | 258.0906 | 65.7 | 3556.5257
|  | 24 | 84.0158 | 267.4925 | 351.0062 | 2452.8 | 258.0906 | 65.7 | 3479.1051
|  | 25 | 55.6334 | 267.4925 | 301.968 | 2452.8 | 258.0906 | 65.7 | 3401.6845
|  | 26 | 27.251 | 267.4925 | 252.9297 | 2452.8 | 258.0906 | 65.7 | 3324.2639
|  | 27 | -1.1314 | 267.4925 | 203.8915 | 2452.8 | 258.0906 | 65.7 | 3246.8432
|  | 28 | -29.5138 | 267.4925 | 154.8533 | 2452.8 | 258.0906 | 65.7 | 3169.4226

## All Season Dengue Endemic_ID
Balance Point Temperature, Annual Variable Degree Days, Thermal Load of Living Space and Annual Electricity Consumption Calculations for Chennai- Baseline and Solar Electricity Scenarios
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | AC hrs/24 hrs (fAC) | Conv (24/1000) KWh |  |  | Annual VCDD |  |  |  | Annual VCDD |  |  |  | Annual VCDD |  | All Other Heat Loads | BE+Other Loads | 10%SF |  | EER | Elec. Cons.
|  | Jan | 22 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9491 | 19 | 254 | [22 empty] | LDRZ Setpoint Adjsuted Preference %
|  | Feb | 22 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9376 | 19 | 239.8 | [22 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Mar | 22 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9205 | 19 | 278.3 | [22 empty] | 22 | 16 | 0.34783
|  | Apr | 22 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8804 | 19 | 268.6 | [22 empty] | 23 | 10 | 0.21739
|  | May | 22 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.7088 | 18.5 | 341.7 | [22 empty] | 24 | 20 | 0.43478
|  | Jun | 22 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.6172 | 18.5 | 307.6 | [23 empty] | 46
|  | July | 22 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.6916 | 18.5 | 296.9
|  | Aug | 22 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8633 | 19 | 296.1
|  | Sep | 22 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.7697 | 19 | 294
|  | Oct | 22 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9319 | 19 | 323.4
|  | Nov | 22 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9434 | 19 | 286.1
|  | Dec | 22 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9548 | 19 | 264.6
|  | Annual VCDD | [9 empty] | 3451.1 | 0.66667 | 0.024 | 3.59 | 12.96 | 3451.1 | 2569.0761 | 3.94 | 12.96 | 3451.1 | 2819.5432 | 2.13 | 41.904 | 3451.1 | 4928.4756 | 3730.8223 | 14047.9173 | 1404.7917 | 15452.709 | 3.1 | 4985 | 22
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 23 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9491 | 20 | 223
|  | Feb | 23 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9376 | 20 | 211.8
|  | Mar | 23 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9205 | 20 | 247.3
|  | Apr | 23 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8804 | 20 | 238.6
|  | May | 23 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.7088 | 19.5 | 310.7
|  | Jun | 23 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.6172 | 19.5 | 277.6
|  | July | 23 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.6916 | 19.5 | 265.9
|  | Aug | 23 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8633 | 20 | 265.1
|  | Sep | 23 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.7697 | 20 | 264
|  | Oct | 23 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9319 | 20 | 292.4
|  | Nov | 23 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9434 | 20 | 256.1
|  | Dec | 23 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9548 | 20 | 233.6
|  | Annual VCDD | [9 empty] | 3086.1 | 0.66667 | 0.024 | 3.59 | 12.96 | 3086.1 | 2297.362 | 3.94 | 12.96 | 3086.1 | 2521.3388 | 2.13 | 41.904 | 3086.1 | 4407.2234 | 3653.4017 | 12879.3258 | 1287.9326 | 14167.2584 | 3.1 | 4570 | 23
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 24 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9491 | 21 | 192
|  | Feb | 24 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9376 | 21 | 183.8
|  | Mar | 24 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9205 | 21 | 216.3
|  | Apr | 24 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8804 | 21 | 208.6
|  | May | 24 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.7088 | 20.5 | 279.7
|  | Jun | 24 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.6172 | 20.5 | 247.6
|  | Jul | 24 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.6916 | 20.5 | 234.9
|  | Aug | 24 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8633 | 21 | 234.1
|  | Sep | 24 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.7697 | 21 | 234
|  | Oct | 24 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9319 | 21 | 261.4
|  | Nov | 24 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9434 | 21 | 226.1
|  | Dec | 24 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9548 | 21 | 202.6
|  | Annual VCDD | [9 empty] | 2721.1 | 0.66667 | 0.024 | 3.59 | 12.96 | 2721.1 | 2025.6478 | 3.94 | 12.96 | 2721.1 | 2223.1343 | 2.13 | 41.904 | 2721.1 | 3885.9711 | 3575.9811 | 11710.7344 | 1171.0734 | 12881.8078 | 3.1 | 4155 | 24
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | [19 empty] | 4533.913 |  |  | MDRZ Setpoint Adjsuted Preference %
|  | Jan | 25 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9491 | 22 | 161 | [22 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Feb | 25 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9376 | 22 | 155.8 | [22 empty] | 25 | 12 | 100
|  | Mar | 25 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9205 | 22 | 185.3
|  | Apr | 25 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8804 | 22 | 178.6
|  | May | 25 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.7088 | 21.5 | 248.7
|  | Jun | 25 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.6172 | 21.5 | 217.6
|  | Jul | 25 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.6916 | 21.5 | 203.9
|  | Aug | 25 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8633 | 22 | 203.1
|  | Sep | 25 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.7697 | 22 | 204
|  | Oct | 25 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9319 | 22 | 230.4
|  | Nov | 25 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9434 | 22 | 196.1
|  | Dec | 25 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9548 | 22 | 171.6
|  | Annual VCDD | [9 empty] | 2356.1 | 0.66667 | 0.024 | 3.59 | 12.96 | 2356.1 | 1753.9336 | 3.94 | 12.96 | 2356.1 | 1924.9299 | 2.13 | 41.904 | 2356.1 | 3364.7189 | 3498.5605 | 10542.1429 | 1054.2143 | 11596.3572 | 3.1 | 3741 | 25 | 792.913
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | [19 empty] | 3741
|  | Jan | 26 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9491 | 23 | 130
|  | Feb | 26 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9376 | 23 | 127.8
|  | Mar | 26 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9205 | 23 | 154.3
|  | Apr | 26 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8804 | 23 | 148.6
|  | May | 26 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.7088 | 22.5 | 217.7
|  | Jun | 26 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.6172 | 22.5 | 187.6
|  | July | 26 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.6916 | 22.5 | 172.9
|  | Aug | 26 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8633 | 23 | 172.1
|  | Sep | 26 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.7697 | 23 | 174
|  | Oct | 26 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9319 | 23 | 199.4
|  | Nov | 26 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9434 | 23 | 166.1
|  | Dec | 26 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9548 | 23 | 140.6
|  | Annual VCDD | [9 empty] | 1991.1 | 0.66667 | 0.024 | 3.59 | 12.96 | 1991.1 | 1482.2194 | 3.94 | 12.96 | 1991.1 | 1626.7255 | 2.13 | 41.904 | 1991.1 | 2843.4667 | 3421.1399 | 9373.5515 | 937.3551 | 10310.9066 | 3.1 | 3326 | 26
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 27 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9491 | 24 | 99 | [22 empty] | HDRZ Setpoint Adjsuted Preference %
|  | Feb | 27 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9376 | 24 | 100 | [22 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Mar | 27 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9205 | 24 | 123.3 | [22 empty] | 26 | 10 | 0.5
|  | Apr | 27 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8804 | 24 | 118.6 | [22 empty] | 27 | 8 | 0.4
|  | May | 27 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.7088 | 23.5 | 186.7 | [22 empty] | 28 | 2 | 0.1
|  | Jun | 27 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.6172 | 23.5 | 157.6 | [23 empty] | 20
|  | Jul | 27 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.6916 | 23.5 | 142.1
|  | Aug | 27 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8633 | 24 | 141.1
|  | Sep | 27 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.7697 | 24 | 144
|  | Oct | 27 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9319 | 24 | 168.4
|  | Nov | 27 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9434 | 24 | 136.1
|  | Dec | 27 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9548 | 24 | 109.7
|  | Annual VCDD | [9 empty] | 1626.6 | 0.66667 | 0.024 | 3.59 | 12.96 | 1626.6 | 1210.8775 | 3.94 | 12.96 | 1626.6 | 1328.9296 | 2.13 | 41.904 | 1626.6 | 2322.9285 | 3343.7192 | 8206.4548 | 820.6455 | 9027.1002 | 3.1 | 2912 | 27
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 28 | 36.6945 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9491 | 25 | 70.2
|  | Feb | 28 | 38.9884 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9376 | 25 | 72.9
|  | Mar | 28 | 42.4274 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9205 | 25 | 93
|  | Apr | 28 | 50.4577 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8804 | 25 | 89.4
|  | May | 28 | 84.8583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.7088 | 24.5 | 155.7
|  | Jun | 28 | 103.2092 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.6172 | 24.5 | 127.7
|  | Jul | 28 | 88.301 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.6916 | 24.5 | 112.3
|  | Aug | 28 | 53.8967 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8633 | 25 | 110.8
|  | Sep | 28 | 72.6583 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.7697 | 25 | 114.5
|  | Oct | 28 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9319 | 25 | 137.8
|  | Nov | 28 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9434 | 25 | 106.4
|  | Dec | 28 | 35.5494 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9548 | 25 | 80.2
|  | Annual VCDD | [9 empty] | 1270.9 | 0.66667 | 0.024 | 3.59 | 12.96 | 1270.9 | 946.0864 | 3.94 | 12.96 | 1270.9 | 1038.3233 | 2.13 | 41.904 | 1270.9 | 1814.9574 | 3266.2986 | 7065.6658 | 706.5666 | 7772.2323 | 3.1 | 2507 | 28
3078.5
1455.413
CLTDgw-avg (°C) for AC Opn hrs. |  | Thermal Conductive Load (TLgw-x) Calculated for Three Climate Zones
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 22°C
AC Opn hrs. | CLTDgw (°C) | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
00.00-01.00 | 1 | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 22 | 3.5 | -1.2 | 4.05 | 3.75 | 1.296 | 496 | 9.7628
01.00-02.00 | 1 | Feb | 31.7 | 7.1 | 3.55 | 28.15 | 1.75 | 22 | 3.5 | -1.25 | 4 | 3.75 | 1.296 | 448 | 8.7091
02.00-03.00 | 0 | Mar | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 22 | 3.5 | -0.85 | 4.4 | 3.75 | 1.296 | 496 | 10.6065
03.00-04.00 | -1 | Apr | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 22 | 3.5 | -0.85 | 4.4 | 3.75 | 1.296 | 480 | 10.2643
04.00-05.00 | -1 | May | 32.4 | 7.7 | 3.85 | 28.55 | 1.75 | 22 | 3.5 | -0.85 | 4.4 | 3.75 | 1.296 | 496 | 10.6065
05.00-06.00 | -1 | Jun | 32.2 | 7.5 | 3.75 | 28.45 | 1.75 | 22 | 3.5 | -0.95 | 4.3 | 3.75 | 1.296 | 480 | 10.031
06.00-07.00 | -1 | Jul | 32.1 | 7.8 | 3.9 | 28.2 | 1.75 | 22 | 3.5 | -1.2 | 4.05 | 3.75 | 1.296 | 496 | 9.7628
07.00-08.00 | -1 | Aug | 32.5 | 8.2 | 4.1 | 28.4 | 1.75 | 22 | 3.5 | -1 | 4.25 | 3.75 | 1.296 | 496 | 10.2449
08.00-09.00 | 0 | Sep | 32.8 | 8.8 | 4.4 | 28.4 | 1.75 | 22 | 3.5 | -1 | 4.25 | 3.75 | 1.296 | 480 | 9.9144
17.00-18.00 | 7 | Oct | 32.5 | 8.5 | 4.25 | 28.25 | 1.75 | 22 | 3.5 | -1.15 | 4.1 | 3.75 | 1.296 | 496 | 9.8833
18.00-19.00 | 7 | Nov | 32.2 | 7.8 | 3.9 | 28.3 | 1.75 | 22 | 3.5 | -1.1 | 4.15 | 3.75 | 1.296 | 480 | 9.6811
19.00-20.00 | 6 | Dec | 32.1 | 7.3 | 3.65 | 28.45 | 1.75 | 22 | 3.5 | -0.95 | 4.3 | 3.75 | 1.296 | 496 | 10.3654
20.00-21.00 | 4 | TLgw-CHN (KWh) | [12 empty] | 119.832
21.00-22.00 | 3 | Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 23°C
22.00-23.00 | 2 | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 23 | 2.5 | -1.2 | 3.05 | 3.75 | 1.296 | 496 | 7.3522
23.00-00.00 | 2 | Feb | 31.7 | 7.1 | 3.55 | 28.15 | 1.75 | 23 | 2.5 | -1.25 | 3 | 3.75 | 1.296 | 448 | 6.5318
CLTDgw-avg (°C) | 1.75 | Mar | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 23 | 2.5 | -0.85 | 3.4 | 3.75 | 1.296 | 496 | 8.1959
|  | Apr | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 23 | 2.5 | -0.85 | 3.4 | 3.75 | 1.296 | 480 | 7.9315
|  | May | 32.4 | 7.7 | 3.85 | 28.55 | 1.75 | 23 | 2.5 | -0.85 | 3.4 | 3.75 | 1.296 | 496 | 8.1959
|  | Jun | 32.2 | 7.5 | 3.75 | 28.45 | 1.75 | 23 | 2.5 | -0.95 | 3.3 | 3.75 | 1.296 | 480 | 7.6982
|  | Jul | 32.1 | 7.8 | 3.9 | 28.2 | 1.75 | 23 | 2.5 | -1.2 | 3.05 | 3.75 | 1.296 | 496 | 7.3522
|  | Aug | 32.5 | 8.2 | 4.1 | 28.4 | 1.75 | 23 | 2.5 | -1 | 3.25 | 3.75 | 1.296 | 496 | 7.8343
|  | Sep | 32.8 | 8.8 | 4.4 | 28.4 | 1.75 | 23 | 2.5 | -1 | 3.25 | 3.75 | 1.296 | 480 | 7.5816
|  | Oct | 32.5 | 8.5 | 4.25 | 28.25 | 1.75 | 23 | 2.5 | -1.15 | 3.1 | 3.75 | 1.296 | 496 | 7.4727
|  | Nov | 32.2 | 7.8 | 3.9 | 28.3 | 1.75 | 23 | 2.5 | -1.1 | 3.15 | 3.75 | 1.296 | 480 | 7.3483
|  | Dec | 32.1 | 7.3 | 3.65 | 28.45 | 1.75 | 23 | 2.5 | -0.95 | 3.3 | 3.75 | 1.296 | 496 | 7.9548
|  | TLgw-CHN (KWh) | [12 empty] | 91.4496
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 24°C
|  | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 24 | 1.5 | -1.2 | 2.05 | 3.75 | 1.296 | 496 | 4.9416
|  | Feb | 31.7 | 7.1 | 3.55 | 28.15 | 1.75 | 24 | 1.5 | -1.25 | 2 | 3.75 | 1.296 | 448 | 4.3546
|  | Mar | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 24 | 1.5 | -0.85 | 2.4 | 3.75 | 1.296 | 496 | 5.7853
|  | Apr | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 24 | 1.5 | -0.85 | 2.4 | 3.75 | 1.296 | 480 | 5.5987
|  | May | 32.4 | 7.7 | 3.85 | 28.55 | 1.75 | 24 | 1.5 | -0.85 | 2.4 | 3.75 | 1.296 | 496 | 5.7853
|  | Jun | 32.2 | 7.5 | 3.75 | 28.45 | 1.75 | 24 | 1.5 | -0.95 | 2.3 | 3.75 | 1.296 | 480 | 5.3654
|  | Jul | 32.1 | 7.8 | 3.9 | 28.2 | 1.75 | 24 | 1.5 | -1.2 | 2.05 | 3.75 | 1.296 | 496 | 4.9416
|  | Aug | 32.5 | 8.2 | 4.1 | 28.4 | 1.75 | 24 | 1.5 | -1 | 2.25 | 3.75 | 1.296 | 496 | 5.4238
|  | Sep | 32.8 | 8.8 | 4.4 | 28.4 | 1.75 | 24 | 1.5 | -1 | 2.25 | 3.75 | 1.296 | 480 | 5.2488
|  | Oct | 32.5 | 8.5 | 4.25 | 28.25 | 1.75 | 24 | 1.5 | -1.15 | 2.1 | 3.75 | 1.296 | 496 | 5.0622
|  | Nov | 32.2 | 7.8 | 3.9 | 28.3 | 1.75 | 24 | 1.5 | -1.1 | 2.15 | 3.75 | 1.296 | 480 | 5.0155
|  | Dec | 32.1 | 7.3 | 3.65 | 28.45 | 1.75 | 24 | 1.5 | -0.95 | 2.3 | 3.75 | 1.296 | 496 | 5.5443
|  | TLgw-AMD (KWh) | [12 empty] | 63.0672
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 25°C
|  | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 25 | 0.5 | -1.2 | 1.05 | 3.75 | 1.296 | 496 | 2.5311
|  | Feb | 31.7 | 7.1 | 3.55 | 28.15 | 1.75 | 25 | 0.5 | -1.25 | 1 | 3.75 | 1.296 | 448 | 2.1773
|  | Mar | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 25 | 0.5 | -0.85 | 1.4 | 3.75 | 1.296 | 496 | 3.3748
|  | Apr | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 25 | 0.5 | -0.85 | 1.4 | 3.75 | 1.296 | 480 | 3.2659
|  | May | 32.4 | 7.7 | 3.85 | 28.55 | 1.75 | 25 | 0.5 | -0.85 | 1.4 | 3.75 | 1.296 | 496 | 3.3748
|  | Jun | 32.2 | 7.5 | 3.75 | 28.45 | 1.75 | 25 | 0.5 | -0.95 | 1.3 | 3.75 | 1.296 | 480 | 3.0326
|  | Jul | 32.1 | 7.8 | 3.9 | 28.2 | 1.75 | 25 | 0.5 | -1.2 | 1.05 | 3.75 | 1.296 | 496 | 2.5311
|  | Aug | 32.5 | 8.2 | 4.1 | 28.4 | 1.75 | 25 | 0.5 | -1 | 1.25 | 3.75 | 1.296 | 496 | 3.0132
|  | Sep | 32.8 | 8.8 | 4.4 | 28.4 | 1.75 | 25 | 0.5 | -1 | 1.25 | 3.75 | 1.296 | 480 | 2.916
|  | Oct | 32.5 | 8.5 | 4.25 | 28.25 | 1.75 | 25 | 0.5 | -1.15 | 1.1 | 3.75 | 1.296 | 496 | 2.6516
|  | Nov | 32.2 | 7.8 | 3.9 | 28.3 | 1.75 | 25 | 0.5 | -1.1 | 1.15 | 3.75 | 1.296 | 480 | 2.6827
|  | Dec | 32.1 | 7.3 | 3.65 | 28.45 | 1.75 | 25 | 0.5 | -0.95 | 1.3 | 3.75 | 1.296 | 496 | 3.1337
|  | TLgw-DEL (KWh) | [12 empty] | 34.6848
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 26°C
|  | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 26 | -0.5 | -1.2 | 0.05 | 3.75 | 1.296 | 496 | 0.12053
|  | Feb | 31.7 | 7.1 | 3.55 | 28.15 | 1.75 | 26 | -0.5 | -1.25 | 0 | 3.75 | 1.296 | 448 | 0
|  | Mar | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 26 | -0.5 | -0.85 | 0.4 | 3.75 | 1.296 | 496 | 0.96422
|  | Apr | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 26 | -0.5 | -0.85 | 0.4 | 3.75 | 1.296 | 480 | 0.93312
|  | May | 32.4 | 7.7 | 3.85 | 28.55 | 1.75 | 26 | -0.5 | -0.85 | 0.4 | 3.75 | 1.296 | 496 | 0.96422
|  | Jun | 32.2 | 7.5 | 3.75 | 28.45 | 1.75 | 26 | -0.5 | -0.95 | 0.3 | 3.75 | 1.296 | 480 | 0.69984
|  | Jul | 32.1 | 7.8 | 3.9 | 28.2 | 1.75 | 26 | -0.5 | -1.2 | 0.05 | 3.75 | 1.296 | 496 | 0.12053
|  | Aug | 32.5 | 8.2 | 4.1 | 28.4 | 1.75 | 26 | -0.5 | -1 | 0.25 | 3.75 | 1.296 | 496 | 0.60264
|  | Sep | 32.8 | 8.8 | 4.4 | 28.4 | 1.75 | 26 | -0.5 | -1 | 0.25 | 3.75 | 1.296 | 480 | 0.5832
|  | Oct | 32.5 | 8.5 | 4.25 | 28.25 | 1.75 | 26 | -0.5 | -1.15 | 0.1 | 3.75 | 1.296 | 496 | 0.24106
|  | Nov | 32.2 | 7.8 | 3.9 | 28.3 | 1.75 | 26 | -0.5 | -1.1 | 0.15 | 3.75 | 1.296 | 480 | 0.34992
|  | Dec | 32.1 | 7.3 | 3.65 | 28.45 | 1.75 | 26 | -0.5 | -0.95 | 0.3 | 3.75 | 1.296 | 496 | 0.72317
|  | TLgw-DEL (KWh) | [12 empty] | 6.3024
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 27°C
|  | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 27 | -1.5 | -1.2 | -0.95 | 3.75 | 1.296 | 496 | -2.29
|  | Feb | 31.7 | 7.1 | 3.55 | 28.15 | 1.75 | 27 | -1.5 | -1.25 | -1 | 3.75 | 1.296 | 448 | -2.1773
|  | Mar | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 27 | -1.5 | -0.85 | -0.6 | 3.75 | 1.296 | 496 | -1.4463
|  | Apr | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 27 | -1.5 | -0.85 | -0.6 | 3.75 | 1.296 | 480 | -1.3997
|  | May | 32.4 | 7.7 | 3.85 | 28.55 | 1.75 | 27 | -1.5 | -0.85 | -0.6 | 3.75 | 1.296 | 496 | -1.4463
|  | Jun | 32.2 | 7.5 | 3.75 | 28.45 | 1.75 | 27 | -1.5 | -0.95 | -0.7 | 3.75 | 1.296 | 480 | -1.633
|  | Jul | 32.1 | 7.8 | 3.9 | 28.2 | 1.75 | 27 | -1.5 | -1.2 | -0.95 | 3.75 | 1.296 | 496 | -2.29
|  | Aug | 32.5 | 8.2 | 4.1 | 28.4 | 1.75 | 27 | -1.5 | -1 | -0.75 | 3.75 | 1.296 | 496 | -1.8079
|  | Sep | 32.8 | 8.8 | 4.4 | 28.4 | 1.75 | 27 | -1.5 | -1 | -0.75 | 3.75 | 1.296 | 480 | -1.7496
|  | Oct | 32.5 | 8.5 | 4.25 | 28.25 | 1.75 | 27 | -1.5 | -1.15 | -0.9 | 3.75 | 1.296 | 496 | -2.1695
|  | Nov | 32.2 | 7.8 | 3.9 | 28.3 | 1.75 | 27 | -1.5 | -1.1 | -0.85 | 3.75 | 1.296 | 480 | -1.9829
|  | Dec | 32.1 | 7.3 | 3.65 | 28.45 | 1.75 | 27 | -1.5 | -0.95 | -0.7 | 3.75 | 1.296 | 496 | -1.6874
|  | TLgw-DEL (KWh) | [12 empty] | -22.08
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 28°C
|  | Jan | 31.6 | 6.8 | 3.4 | 28.2 | 1.75 | 28 | -2.5 | -1.2 | -1.95 | 3.75 | 1.296 | 496 | -4.7006
|  | Feb | 31.7 | 7.1 | 3.55 | 28.15 | 1.75 | 28 | -2.5 | -1.25 | -2 | 3.75 | 1.296 | 448 | -4.3546
|  | Mar | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 28 | -2.5 | -0.85 | -1.6 | 3.75 | 1.296 | 496 | -3.8569
|  | Apr | 32.2 | 7.3 | 3.65 | 28.55 | 1.75 | 28 | -2.5 | -0.85 | -1.6 | 3.75 | 1.296 | 480 | -3.7325
|  | May | 32.4 | 7.7 | 3.85 | 28.55 | 1.75 | 28 | -2.5 | -0.85 | -1.6 | 3.75 | 1.296 | 496 | -3.8569
|  | Jun | 32.2 | 7.5 | 3.75 | 28.45 | 1.75 | 28 | -2.5 | -0.95 | -1.7 | 3.75 | 1.296 | 480 | -3.9658
|  | Jul | 32.1 | 7.8 | 3.9 | 28.2 | 1.75 | 28 | -2.5 | -1.2 | -1.95 | 3.75 | 1.296 | 496 | -4.7006
|  | Aug | 32.5 | 8.2 | 4.1 | 28.4 | 1.75 | 28 | -2.5 | -1 | -1.75 | 3.75 | 1.296 | 496 | -4.2185
|  | Sep | 32.8 | 8.8 | 4.4 | 28.4 | 1.75 | 28 | -2.5 | -1 | -1.75 | 3.75 | 1.296 | 480 | -4.0824
|  | Oct | 32.5 | 8.5 | 4.25 | 28.25 | 1.75 | 28 | -2.5 | -1.15 | -1.9 | 3.75 | 1.296 | 496 | -4.5801
|  | Nov | 32.2 | 7.8 | 3.9 | 28.3 | 1.75 | 28 | -2.5 | -1.1 | -1.85 | 3.75 | 1.296 | 480 | -4.3157
|  | Dec | 32.1 | 7.3 | 3.65 | 28.45 | 1.75 | 28 | -2.5 | -0.95 | -1.7 | 3.75 | 1.296 | 496 | -4.098
|  | TLgw-DEL (KWh) | [12 empty] | -50.4624
Annual Radiation Thermal Load Through Glass Window
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jan | 0.55 | 0.51 | 100.94 | 1.296 | 496 | 18.2005
|  | Feb | 0.55 | 0.51 | 107.25 | 1.296 | 448 | 17.4668
|  | Mar | 0.55 | 0.51 | 116.71 | 1.296 | 496 | 21.044
|  | Apr | 0.55 | 0.51 | 138.8 | 1.296 | 480 | 24.2197
|  | May | 0.55 | 0.51 | 233.43 | 1.296 | 496 | 42.0897
|  | Jun | 0.55 | 0.51 | 283.91 | 1.296 | 480 | 49.5404
|  | Jul | 0.55 | 0.51 | 242.9 | 1.296 | 496 | 43.7973
|  | Aug | 0.55 | 0.51 | 148.26 | 1.296 | 496 | 26.7327
|  | Sep | 0.55 | 0.51 | 199.87 | 1.296 | 480 | 34.876
|  | Oct | 0.55 | 0.51 | 110.41 | 1.296 | 496 | 19.908
|  | Nov | 0.55 | 0.51 | 104.1 | 1.296 | 480 | 18.1648
|  | Dec | 0.55 | 0.51 | 97.79 | 1.296 | 496 | 17.6325
|  | TLrad | [5 empty] | 333.6724
Inflitration Load for Different Setpoint Temperatures
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) |  | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 22 | 9.6 | 291.0136 |  | 0.277 | 80.6108 | 496 | 39.9829
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 22 | 9.7 | 294.045 |  | 0.277 | 81.4505 | 448 | 36.4898
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 22 | 10.2 | 309.202 |  | 0.277 | 85.6489 | 496 | 42.4819
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 22 | 10.2 | 309.202 |  | 0.277 | 85.6489 | 480 | 41.1115
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.4 | 22 | 10.4 | 315.2648 |  | 0.277 | 87.3283 | 496 | 43.3149
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 22 | 10.2 | 309.202 |  | 0.277 | 85.6489 | 480 | 41.1115
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 22 | 10.1 | 306.1706 |  | 0.277 | 84.8093 | 496 | 42.0654
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 22 | 10.5 | 318.2962 |  | 0.277 | 88.168 | 496 | 43.7313
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.8 | 22 | 10.8 | 327.3903 |  | 0.277 | 90.6871 | 480 | 43.5298
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 22 | 10.5 | 318.2962 |  | 0.277 | 88.168 | 496 | 43.7313
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 22 | 10.2 | 309.202 |  | 0.277 | 85.6489 | 480 | 41.1115
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 22 | 10.1 | 306.1706 |  | 0.277 | 84.8093 | 496 | 42.0654
|  | Tinf for setpoint 22 degrees C | [12 empty] | 500.7273
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 23 | 8.6 | 260.6997 |  | 0.277 | 72.2138 | 496 | 35.8181
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 23 | 8.7 | 263.7311 |  | 0.277 | 73.0535 | 448 | 32.728
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 23 | 9.2 | 278.8881 |  | 0.277 | 77.252 | 496 | 38.317
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 23 | 9.2 | 278.8881 |  | 0.277 | 77.252 | 480 | 37.081
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.4 | 23 | 9.4 | 284.9508 |  | 0.277 | 78.9314 | 496 | 39.15
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 23 | 9.2 | 278.8881 |  | 0.277 | 77.252 | 480 | 37.081
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 23 | 9.1 | 275.8567 |  | 0.277 | 76.4123 | 496 | 37.9005
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 23 | 9.5 | 287.9822 |  | 0.277 | 79.7711 | 496 | 39.5665
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.8 | 23 | 9.8 | 297.0764 |  | 0.277 | 82.2902 | 480 | 39.4993
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 23 | 9.5 | 287.9822 |  | 0.277 | 79.7711 | 496 | 39.5665
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 23 | 9.2 | 278.8881 |  | 0.277 | 77.252 | 480 | 37.081
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 23 | 9.1 | 275.8567 |  | 0.277 | 76.4123 | 496 | 37.9005
|  | Tinf for setpoint 23 degrees C | [12 empty] | 451.689
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 24 | 7.6 | 230.3858 |  | 0.277 | 63.8169 | 496 | 31.6532
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 24 | 7.7 | 233.4172 |  | 0.277 | 64.6566 | 448 | 28.9661
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 24 | 8.2 | 248.5741 |  | 0.277 | 68.855 | 496 | 34.1521
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 24 | 8.2 | 248.5741 |  | 0.277 | 68.855 | 480 | 33.0504
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.4 | 24 | 8.4 | 254.6369 |  | 0.277 | 70.5344 | 496 | 34.9851
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 24 | 8.2 | 248.5741 |  | 0.277 | 68.855 | 480 | 33.0504
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 24 | 8.1 | 245.5427 |  | 0.277 | 68.0153 | 496 | 33.7356
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 24 | 8.5 | 257.6683 |  | 0.277 | 71.3741 | 496 | 35.4016
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.8 | 24 | 8.8 | 266.7625 |  | 0.277 | 73.8932 | 480 | 35.4687
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 24 | 8.5 | 257.6683 |  | 0.277 | 71.3741 | 496 | 35.4016
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 24 | 8.2 | 248.5741 |  | 0.277 | 68.855 | 480 | 33.0504
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 24 | 8.1 | 245.5427 |  | 0.277 | 68.0153 | 496 | 33.7356
|  | Tinf for setpoint 24 degrees C | [12 empty] | 402.6508
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 25 | 6.6 | 200.0719 |  | 0.277 | 55.4199 | 496 | 27.4883
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 25 | 6.7 | 203.1033 |  | 0.277 | 56.2596 | 448 | 25.2043
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 25 | 7.2 | 218.2602 |  | 0.277 | 60.4581 | 496 | 29.9872
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 25 | 7.2 | 218.2602 |  | 0.277 | 60.4581 | 480 | 29.0199
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.4 | 25 | 7.4 | 224.323 |  | 0.277 | 62.1375 | 496 | 30.8202
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 25 | 7.2 | 218.2602 |  | 0.277 | 60.4581 | 480 | 29.0199
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 25 | 7.1 | 215.2288 |  | 0.277 | 59.6184 | 496 | 29.5707
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 25 | 7.5 | 227.3544 |  | 0.277 | 62.9772 | 496 | 31.2367
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.8 | 25 | 7.8 | 236.4486 |  | 0.277 | 65.4963 | 480 | 31.4382
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 25 | 7.5 | 227.3544 |  | 0.277 | 62.9772 | 496 | 31.2367
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 25 | 7.2 | 218.2602 |  | 0.277 | 60.4581 | 480 | 29.0199
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 25 | 7.1 | 215.2288 |  | 0.277 | 59.6184 | 496 | 29.5707
|  | Tinf for setpoint 25 degrees C | [12 empty] | 353.6126
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 26 | 5.6 | 169.7579 |  | 0.277 | 47.023 | 496 | 23.3234
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 26 | 5.7 | 172.7893 |  | 0.277 | 47.8626 | 448 | 21.4425
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 26 | 6.2 | 187.9463 |  | 0.277 | 52.0611 | 496 | 25.8223
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 26 | 6.2 | 187.9463 |  | 0.277 | 52.0611 | 480 | 24.9893
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.4 | 26 | 6.4 | 194.0091 |  | 0.277 | 53.7405 | 496 | 26.6553
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 26 | 6.2 | 187.9463 |  | 0.277 | 52.0611 | 480 | 24.9893
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 26 | 6.1 | 184.9149 |  | 0.277 | 51.2214 | 496 | 25.4058
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 26 | 6.5 | 197.0405 |  | 0.277 | 54.5802 | 496 | 27.0718
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.8 | 26 | 6.8 | 206.1347 |  | 0.277 | 57.0993 | 480 | 27.4077
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 26 | 6.5 | 197.0405 |  | 0.277 | 54.5802 | 496 | 27.0718
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 26 | 6.2 | 187.9463 |  | 0.277 | 52.0611 | 480 | 24.9893
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 26 | 6.1 | 184.9149 |  | 0.277 | 51.2214 | 496 | 25.4058
|  | Tinf for setpoint 26 degrees C | [12 empty] | 304.5744
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 27 | 4.6 | 139.444 |  | 0.277 | 38.626 | 496 | 19.1585
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 27 | 4.7 | 142.4754 |  | 0.277 | 39.4657 | 448 | 17.6806
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 27 | 5.2 | 157.6324 |  | 0.277 | 43.6642 | 496 | 21.6574
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 27 | 5.2 | 157.6324 |  | 0.277 | 43.6642 | 480 | 20.9588
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.4 | 27 | 5.4 | 163.6952 |  | 0.277 | 45.3436 | 496 | 22.4904
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 27 | 5.2 | 157.6324 |  | 0.277 | 43.6642 | 480 | 20.9588
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 27 | 5.1 | 154.601 |  | 0.277 | 42.8245 | 496 | 21.2409
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 27 | 5.5 | 166.7266 |  | 0.277 | 46.1833 | 496 | 22.9069
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.8 | 27 | 5.8 | 175.8207 |  | 0.277 | 48.7023 | 480 | 23.3771
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 27 | 5.5 | 166.7266 |  | 0.277 | 46.1833 | 496 | 22.9069
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 27 | 5.2 | 157.6324 |  | 0.277 | 43.6642 | 480 | 20.9588
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 27 | 5.1 | 154.601 |  | 0.277 | 42.8245 | 496 | 21.2409
|  | Tinf for setpoint 27 degrees C | [12 empty] | 255.5362
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 31.6 | 28 | 3.6 | 109.1301 |  | 0.277 | 30.229 | 496 | 14.9936
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 31.7 | 28 | 3.7 | 112.1615 |  | 0.277 | 31.0687 | 448 | 13.9188
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 28 | 4.2 | 127.3185 |  | 0.277 | 35.2672 | 496 | 17.4925
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 28 | 4.2 | 127.3185 |  | 0.277 | 35.2672 | 480 | 16.9283
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 32.4 | 28 | 4.4 | 133.3812 |  | 0.277 | 36.9466 | 496 | 18.3255
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 28 | 4.2 | 127.3185 |  | 0.277 | 35.2672 | 480 | 16.9283
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 28 | 4.1 | 124.2871 |  | 0.277 | 34.4275 | 496 | 17.076
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 28 | 4.5 | 136.4126 |  | 0.277 | 37.7863 | 496 | 18.742
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.8 | 28 | 4.8 | 145.5068 |  | 0.277 | 40.3054 | 480 | 19.3466
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 32.5 | 28 | 4.5 | 136.4126 |  | 0.277 | 37.7863 | 496 | 18.742
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 28 | 4.2 | 127.3185 |  | 0.277 | 35.2672 | 480 | 16.9283
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 32.1 | 28 | 4.1 | 124.2871 |  | 0.277 | 34.4275 | 496 | 17.076
|  | Tinf for setpoint 28 degrees C | [12 empty] | 206.4979
Total Internal Load by People
|  | Month | People | SenL/person | CLF | SensL (W) | Latent/Person | LatentL (W) | Total peo L (W) | AC opn hrs |  | Total PL (KWh)
|  | Jan | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Feb | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 448 |  | 188.16
|  | Mar | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Apr | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | May | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Jun | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Jul | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Aug | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Sep | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Oct | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Nov | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Dec | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Total Internal Load by People | [9 empty] | 2452.8
Total Internal Heat Load of Lights per Year
|  | No. Bulbs | Watt Rating | bf | Fu | CLF | hrs (6hrs/day) | Tihlig(KWh)
|  | 3 | 60 | 1.24 | 0.66 | 0.8 | 2190 | 258.0906
|  | Total Internal Heat Load of Lights per Year | [5 empty] | 258.0906
Total Internal Heat Load-Equipment
|  | TV Rating W | Hrs /day | Total hrs | Tihe (KWh)
|  | 36 | 5 | 1825 | 65.7
|  | Total load Equipment |  |  | 65.7
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 22 | 119.832 | 333.6724 | 500.7273 | 2452.8 | 258.0906 | 65.7 | 3730.8223
|  | 23 | 91.4496 | 333.6724 | 451.689 | 2452.8 | 258.0906 | 65.7 | 3653.4017
|  | 24 | 63.0672 | 333.6724 | 402.6508 | 2452.8 | 258.0906 | 65.7 | 3575.9811
|  | 25 | 34.6848 | 333.6724 | 353.6126 | 2452.8 | 258.0906 | 65.7 | 3498.5605
|  | 26 | 6.3024 | 333.6724 | 304.5744 | 2452.8 | 258.0906 | 65.7 | 3421.1399
|  | 27 | -22.08 | 333.6724 | 255.5362 | 2452.8 | 258.0906 | 65.7 | 3343.7192
|  | 28 | -50.4624 | 333.6724 | 206.4979 | 2452.8 | 258.0906 | 65.7 | 3266.2986

## All Season Dengue Endemic_MM
Balance Point Temperature, Annual Variable Degree Days, Thermal Load of Living Space and Annual Electricity Consumption Calculations for Chennai- Baseline and Solar Electricity Scenarios
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | AC hrs/24 hrs (fAC) | Conv (24/1000) KWh |  |  | Annual VCDD |  |  |  | Annual VCDD |  |  |  | Annual VCDD |  | All Other Heat Loads | BE+Other Loads | 10%SF |  | EER | Elec. Cons.
|  | Jan | 22 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9605 | 19 | 206 | [22 empty] | LDRZ Setpoint Adjsuted Preference %
|  | Feb | 22 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9434 | 19 | 240.4 | [22 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Mar | 22 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9319 | 19 | 328.3 | [22 empty] | 22 | 16 | 0.34783
|  | Apr | 22 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.909 | 19 | 317.6 | [22 empty] | 23 | 10 | 0.21739
|  | May | 22 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8347 | 19 | 360.1 | [22 empty] | 24 | 20 | 0.43478
|  | Jun | 22 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.7545 | 19 | 259 | [23 empty] | 46
|  | July | 22 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8175 | 19 | 254.5
|  | Aug | 22 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.8976 | 19 | 258.6
|  | Sep | 22 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9262 | 19 | 256.8
|  | Oct | 22 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9434 | 19 | 291.7
|  | Nov | 22 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9605 | 19 | 264.1
|  | Dec | 22 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 18.9662 | 19 | 256.9
|  | Annual VCDD | [9 empty] | 3294 | 0.66667 | 0.024 | 3.59 | 12.96 | 3294 | 2452.1274 | 3.94 | 12.96 | 3294 | 2691.1927 | 2.13 | 41.904 | 3294 | 4704.1229 | 3202.8963 | 13050.3393 | 1305.0339 | 14355.3732 | 3.1 | 4631 | 22
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 23 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9605 | 20 | 175.9
|  | Feb | 23 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9434 | 20 | 212.5
|  | Mar | 23 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9319 | 20 | 297.3
|  | Apr | 23 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.909 | 20 | 287.6
|  | May | 23 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8347 | 20 | 329.1
|  | Jun | 23 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.7545 | 20 | 229
|  | July | 23 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8175 | 20 | 223.5
|  | Aug | 23 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.8976 | 20 | 227.6
|  | Sep | 23 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9262 | 20 | 226.8
|  | Oct | 23 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9434 | 20 | 260.7
|  | Nov | 23 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9605 | 20 | 234.1
|  | Dec | 23 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 19.9662 | 20 | 225.9
|  | Annual VCDD | [9 empty] | 2930 | 0.66667 | 0.024 | 3.59 | 12.96 | 2930 | 2181.1576 | 3.94 | 12.96 | 2930 | 2393.8053 | 2.13 | 41.904 | 2930 | 4184.2988 | 3174.5139 | 11933.7756 | 1193.3776 | 13127.1532 | 3.1 | 4235 | 23
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 24 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9605 | 21 | 147.4
|  | Feb | 24 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9434 | 21 | 184.7
|  | Mar | 24 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9319 | 21 | 266.3
|  | Apr | 24 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.909 | 21 | 257.6
|  | May | 24 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8347 | 21 | 298.1
|  | Jun | 24 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.7545 | 21 | 199
|  | Jul | 24 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8175 | 21 | 192.5
|  | Aug | 24 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.8976 | 21 | 196.6
|  | Sep | 24 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9262 | 21 | 196.8
|  | Oct | 24 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9434 | 21 | 229.7
|  | Nov | 24 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9605 | 21 | 204.1
|  | Dec | 24 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 20.9662 | 21 | 195
|  | Annual VCDD | [9 empty] | 2567.8 | 0.66667 | 0.024 | 3.59 | 12.96 | 2567.8 | 1911.5278 | 3.94 | 12.96 | 2567.8 | 2097.8885 | 2.13 | 41.904 | 2567.8 | 3667.0452 | 3146.1315 | 10822.593 | 1082.2593 | 11904.8523 | 3.1 | 3840 | 24
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | [19 empty] | 4201 |  |  | MDRZ Setpoint Adjsuted Preference %
|  | Jan | 25 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9605 | 22 | 121.6 | [22 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Feb | 25 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9434 | 22 | 158 | [22 empty] | 25 | 12 | 100
|  | Mar | 25 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9319 | 22 | 235.3
|  | Apr | 25 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.909 | 22 | 227.6
|  | May | 25 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8347 | 22 | 267.1 | [21 empty] | 751
|  | Jun | 25 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.7545 | 22 | 169
|  | Jul | 25 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8175 | 22 | 161.5
|  | Aug | 25 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.8976 | 22 | 165.6
|  | Sep | 25 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9262 | 22 | 166.8
|  | Oct | 25 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9434 | 22 | 198.7
|  | Nov | 25 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9605 | 22 | 174.2
|  | Dec | 25 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 21.9662 | 22 | 164.3
|  | Annual VCDD | [9 empty] | 2209.7 | 0.66667 | 0.024 | 3.59 | 12.96 | 2209.7 | 1644.9502 | 3.94 | 12.96 | 2209.7 | 1805.3214 | 2.13 | 41.904 | 2209.7 | 3155.6468 | 3117.7491 | 9723.6674 | 972.3667 | 10696.0341 | 3.1 | 3450 | 25
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth | [19 empty] | 3450
|  | Jan | 26 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9605 | 23 | 134.6
|  | Feb | 26 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9434 | 23 | 98
|  | Mar | 26 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9319 | 23 | 132.7
|  | Apr | 26 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.909 | 23 | 204.3
|  | May | 26 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8347 | 23 | 197.6
|  | Jun | 26 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.7545 | 23 | 236.1
|  | July | 26 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8175 | 23 | 139
|  | Aug | 26 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.8976 | 23 | 130.5
|  | Sep | 26 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9262 | 23 | 134.6
|  | Oct | 26 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9434 | 23 | 136.8
|  | Nov | 26 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9605 | 23 | 167.7
|  | Dec | 26 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 22.9662 | 23 | 144.8
|  | Annual VCDD | [9 empty] | 1856.7 | 0.66667 | 0.024 | 3.59 | 12.96 | 1856.7 | 1382.1691 | 3.94 | 12.96 | 1856.7 | 1516.9209 | 2.13 | 41.904 | 1856.7 | 2651.5316 | 3089.3667 | 8639.9883 | 863.9988 | 9503.9871 | 3.1 | 3066 | 26
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 27 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9605 | 24 | 77.8 | [22 empty] | HDRZ Setpoint Adjsuted Preference %
|  | Feb | 27 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9434 | 24 | 109.4 | [22 empty] | AC Setpoint Temp (°C) | % Preference | Adj Pref. %
|  | Mar | 27 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9319 | 24 | 173.6 | [22 empty] | 26 | 10 | 0.5
|  | Apr | 27 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.909 | 24 | 167.6 | [22 empty] | 27 | 8 | 0.4
|  | May | 27 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8347 | 24 | 205.1 | [22 empty] | 28 | 2 | 0.1
|  | Jun | 27 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.7545 | 24 | 109 | [23 empty] | 20
|  | Jul | 27 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8175 | 24 | 99.5
|  | Aug | 27 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.8976 | 24 | 103.6
|  | Sep | 27 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9262 | 24 | 106.8
|  | Oct | 27 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9434 | 24 | 136.7
|  | Nov | 27 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9605 | 24 | 116.5
|  | Dec | 27 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 23.9662 | 24 | 105.7
|  | Annual VCDD | [9 empty] | 1511.3 | 0.66667 | 0.024 | 3.59 | 12.96 | 1511.3 | 1125.0456 | 3.94 | 12.96 | 1511.3 | 1234.7297 | 2.13 | 41.904 | 1511.3 | 2158.2699 | 3060.9843 | 7579.0294 | 757.9029 | 8336.9323 | 3.1 | 2689 | 27
|  | Month | [7 empty] | Tbal-m Calc. | Tbal-m taken | VCDDmth
|  | Jan | 28 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9605 | 25 | 60
|  | Feb | 28 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9434 | 25 | 89.2
|  | Mar | 28 | 40.1371 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9319 | 25 | 143.9
|  | Apr | 28 | 44.7212 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.909 | 25 | 137.6
|  | May | 28 | 59.6295 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8347 | 25 | 174.1
|  | Jun | 28 | 75.6865 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.7545 | 25 | 79
|  | Jul | 28 | 63.0721 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8175 | 25 | 68.6
|  | Aug | 28 | 47.0151 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.8976 | 25 | 72.6
|  | Sep | 28 | 41.2822 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9262 | 25 | 76.8
|  | Oct | 28 | 37.8433 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9434 | 25 | 105.7
|  | Nov | 28 | 34.4007 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9605 | 25 | 90.1
|  | Dec | 28 | 33.2555 | 420 | 118.8 | 36 | 191.96 | 8.47 | 24.9662 | 25 | 80.8
|  | Annual VCDD | [9 empty] | 1178.4 | 0.66667 | 0.024 | 3.59 | 12.96 | 1178.4 | 877.2274 | 3.94 | 12.96 | 1178.4 | 962.7509 | 2.13 | 41.904 | 1178.4 | 1682.8593 | 3032.6019 | 6555.4394 | 655.5439 | 7210.9834 | 3.1 | 2326 | 28
[32 empty] | 2841.2 |  | 1359.8
CLTDgw-avg (°C) for AC Opn hrs. |  | Thermal Conductive Load (TLgw-x) Calculated for Three Climate Zones
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 22°C
AC Opn hrs. | CLTDgw (°C) | Month | Tmax (°C) | DR | DR/2 | TM = Tmax-(DR/2) | CLTDgw-avg (°C) | TSP (°C) | 25.5-TSP (°C) | TM-29.4 (°C) | CLTDglasscorr | Ugw-non op (W/m2°C) | Agw-nonop (m2) | AC-hrs/Month | TLgw (monthly)-KWh
00.00-01.00 | 1 | Jan | 33.2 | 12.6 | 6.3 | 26.9 | 1.75 | 22 | 3.5 | -2.5 | 2.75 | 3.75 | 1.296 | 496 | 6.629
01.00-02.00 | 1 | Feb | 35.9 | 13.7 | 6.85 | 29.05 | 1.75 | 22 | 3.5 | -0.35 | 4.9 | 3.75 | 1.296 | 448 | 10.6687
02.00-03.00 | 0 | Mar | 37.1 | 13 | 6.5 | 30.6 | 1.75 | 22 | 3.5 | 1.2 | 6.45 | 3.75 | 1.296 | 496 | 15.5481
03.00-04.00 | -1 | Apr | 38.9 | 11.7 | 5.85 | 33.05 | 1.75 | 22 | 3.5 | 3.65 | 8.9 | 3.75 | 1.296 | 480 | 20.7619
04.00-05.00 | -1 | May | 37.8 | 8.1 | 4.05 | 33.75 | 1.75 | 22 | 3.5 | 4.35 | 9.6 | 3.75 | 1.296 | 496 | 23.1414
05.00-06.00 | -1 | Jun | 32.2 | 5.6 | 2.8 | 29.4 | 1.75 | 22 | 3.5 | 0 | 5.25 | 3.75 | 1.296 | 480 | 12.2472
06.00-07.00 | -1 | Jul | 31.9 | 5.2 | 2.6 | 29.3 | 1.75 | 22 | 3.5 | -0.1 | 5.15 | 3.75 | 1.296 | 496 | 12.4144
07.00-08.00 | -1 | Aug | 31.2 | 4.9 | 2.45 | 28.75 | 1.75 | 22 | 3.5 | -0.65 | 4.6 | 3.75 | 1.296 | 496 | 11.0886
08.00-09.00 | 0 | Sep | 32.2 | 5.7 | 2.85 | 29.35 | 1.75 | 22 | 3.5 | -0.05 | 5.2 | 3.75 | 1.296 | 480 | 12.1306
17.00-18.00 | 7 | Oct | 33.4 | 7.1 | 3.55 | 29.85 | 1.75 | 22 | 3.5 | 0.45 | 5.7 | 3.75 | 1.296 | 496 | 13.7402
18.00-19.00 | 7 | Nov | 33.9 | 9 | 4.5 | 29.4 | 1.75 | 22 | 3.5 | 0 | 5.25 | 3.75 | 1.296 | 480 | 12.2472
19.00-20.00 | 6 | Dec | 33.2 | 11.3 | 5.65 | 27.55 | 1.75 | 22 | 3.5 | -1.85 | 3.4 | 3.75 | 1.296 | 496 | 8.1959
20.00-21.00 | 4 | TLgw-CHN (KWh) | [12 empty] | 158.8131
21.00-22.00 | 3 | Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 23°C
22.00-23.00 | 2 | Jan | 33.2 | 12.6 | 6.3 | 26.9 | 1.75 | 23 | 2.5 | -2.5 | 1.75 | 3.75 | 1.296 | 496 | 4.2185
23.00-00.00 | 2 | Feb | 35.9 | 13.7 | 6.85 | 29.05 | 1.75 | 23 | 2.5 | -0.35 | 3.9 | 3.75 | 1.296 | 448 | 8.4914
CLTDgw-avg (°C) | 1.75 | Mar | 37.1 | 13 | 6.5 | 30.6 | 1.75 | 23 | 2.5 | 1.2 | 5.45 | 3.75 | 1.296 | 496 | 13.1376
|  | Apr | 38.9 | 11.7 | 5.85 | 33.05 | 1.75 | 23 | 2.5 | 3.65 | 7.9 | 3.75 | 1.296 | 480 | 18.4291
|  | May | 37.8 | 8.1 | 4.05 | 33.75 | 1.75 | 23 | 2.5 | 4.35 | 8.6 | 3.75 | 1.296 | 496 | 20.7308
|  | Jun | 32.2 | 5.6 | 2.8 | 29.4 | 1.75 | 23 | 2.5 | 0 | 4.25 | 3.75 | 1.296 | 480 | 9.9144
|  | Jul | 31.9 | 5.2 | 2.6 | 29.3 | 1.75 | 23 | 2.5 | -0.1 | 4.15 | 3.75 | 1.296 | 496 | 10.0038
|  | Aug | 31.2 | 4.9 | 2.45 | 28.75 | 1.75 | 23 | 2.5 | -0.65 | 3.6 | 3.75 | 1.296 | 496 | 8.678
|  | Sep | 32.2 | 5.7 | 2.85 | 29.35 | 1.75 | 23 | 2.5 | -0.05 | 4.2 | 3.75 | 1.296 | 480 | 9.7978
|  | Oct | 33.4 | 7.1 | 3.55 | 29.85 | 1.75 | 23 | 2.5 | 0.45 | 4.7 | 3.75 | 1.296 | 496 | 11.3296
|  | Nov | 33.9 | 9 | 4.5 | 29.4 | 1.75 | 23 | 2.5 | 0 | 4.25 | 3.75 | 1.296 | 480 | 9.9144
|  | Dec | 33.2 | 11.3 | 5.65 | 27.55 | 1.75 | 23 | 2.5 | -1.85 | 2.4 | 3.75 | 1.296 | 496 | 5.7853
|  | TLgw-CHN (KWh) | [12 empty] | 130.4307
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 24°C
|  | Jan | 33.2 | 12.6 | 6.3 | 26.9 | 1.75 | 24 | 1.5 | -2.5 | 0.75 | 3.75 | 1.296 | 496 | 1.8079
|  | Feb | 35.9 | 13.7 | 6.85 | 29.05 | 1.75 | 24 | 1.5 | -0.35 | 2.9 | 3.75 | 1.296 | 448 | 6.3141
|  | Mar | 37.1 | 13 | 6.5 | 30.6 | 1.75 | 24 | 1.5 | 1.2 | 4.45 | 3.75 | 1.296 | 496 | 10.727
|  | Apr | 38.9 | 11.7 | 5.85 | 33.05 | 1.75 | 24 | 1.5 | 3.65 | 6.9 | 3.75 | 1.296 | 480 | 16.0963
|  | May | 37.8 | 8.1 | 4.05 | 33.75 | 1.75 | 24 | 1.5 | 4.35 | 7.6 | 3.75 | 1.296 | 496 | 18.3203
|  | Jun | 32.2 | 5.6 | 2.8 | 29.4 | 1.75 | 24 | 1.5 | 0 | 3.25 | 3.75 | 1.296 | 480 | 7.5816
|  | Jul | 31.9 | 5.2 | 2.6 | 29.3 | 1.75 | 24 | 1.5 | -0.1 | 3.15 | 3.75 | 1.296 | 496 | 7.5933
|  | Aug | 31.2 | 4.9 | 2.45 | 28.75 | 1.75 | 24 | 1.5 | -0.65 | 2.6 | 3.75 | 1.296 | 496 | 6.2675
|  | Sep | 32.2 | 5.7 | 2.85 | 29.35 | 1.75 | 24 | 1.5 | -0.05 | 3.2 | 3.75 | 1.296 | 480 | 7.465
|  | Oct | 33.4 | 7.1 | 3.55 | 29.85 | 1.75 | 24 | 1.5 | 0.45 | 3.7 | 3.75 | 1.296 | 496 | 8.9191
|  | Nov | 33.9 | 9 | 4.5 | 29.4 | 1.75 | 24 | 1.5 | 0 | 3.25 | 3.75 | 1.296 | 480 | 7.5816
|  | Dec | 33.2 | 11.3 | 5.65 | 27.55 | 1.75 | 24 | 1.5 | -1.85 | 1.4 | 3.75 | 1.296 | 496 | 3.3748
|  | TLgw-AMD (KWh) | [12 empty] | 102.0483
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 25°C
|  | Jan | 33.2 | 12.6 | 6.3 | 26.9 | 1.75 | 25 | 0.5 | -2.5 | -0.25 | 3.75 | 1.296 | 496 | -0.60264
|  | Feb | 35.9 | 13.7 | 6.85 | 29.05 | 1.75 | 25 | 0.5 | -0.35 | 1.9 | 3.75 | 1.296 | 448 | 4.1368
|  | Mar | 37.1 | 13 | 6.5 | 30.6 | 1.75 | 25 | 0.5 | 1.2 | 3.45 | 3.75 | 1.296 | 496 | 8.3164
|  | Apr | 38.9 | 11.7 | 5.85 | 33.05 | 1.75 | 25 | 0.5 | 3.65 | 5.9 | 3.75 | 1.296 | 480 | 13.7635
|  | May | 37.8 | 8.1 | 4.05 | 33.75 | 1.75 | 25 | 0.5 | 4.35 | 6.6 | 3.75 | 1.296 | 496 | 15.9097
|  | Jun | 32.2 | 5.6 | 2.8 | 29.4 | 1.75 | 25 | 0.5 | 0 | 2.25 | 3.75 | 1.296 | 480 | 5.2488
|  | Jul | 31.9 | 5.2 | 2.6 | 29.3 | 1.75 | 25 | 0.5 | -0.1 | 2.15 | 3.75 | 1.296 | 496 | 5.1827
|  | Aug | 31.2 | 4.9 | 2.45 | 28.75 | 1.75 | 25 | 0.5 | -0.65 | 1.6 | 3.75 | 1.296 | 496 | 3.8569
|  | Sep | 32.2 | 5.7 | 2.85 | 29.35 | 1.75 | 25 | 0.5 | -0.05 | 2.2 | 3.75 | 1.296 | 480 | 5.1322
|  | Oct | 33.4 | 7.1 | 3.55 | 29.85 | 1.75 | 25 | 0.5 | 0.45 | 2.7 | 3.75 | 1.296 | 496 | 6.5085
|  | Nov | 33.9 | 9 | 4.5 | 29.4 | 1.75 | 25 | 0.5 | 0 | 2.25 | 3.75 | 1.296 | 480 | 5.2488
|  | Dec | 33.2 | 11.3 | 5.65 | 27.55 | 1.75 | 25 | 0.5 | -1.85 | 0.4 | 3.75 | 1.296 | 496 | 0.96422
|  | TLgw-DEL (KWh) | [12 empty] | 73.6659
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 26°C
|  | Jan | 33.2 | 12.6 | 6.3 | 26.9 | 1.75 | 26 | -0.5 | -2.5 | -1.25 | 3.75 | 1.296 | 496 | -3.0132
|  | Feb | 35.9 | 13.7 | 6.85 | 29.05 | 1.75 | 26 | -0.5 | -0.35 | 0.9 | 3.75 | 1.296 | 448 | 1.9596
|  | Mar | 37.1 | 13 | 6.5 | 30.6 | 1.75 | 26 | -0.5 | 1.2 | 2.45 | 3.75 | 1.296 | 496 | 5.9059
|  | Apr | 38.9 | 11.7 | 5.85 | 33.05 | 1.75 | 26 | -0.5 | 3.65 | 4.9 | 3.75 | 1.296 | 480 | 11.4307
|  | May | 37.8 | 8.1 | 4.05 | 33.75 | 1.75 | 26 | -0.5 | 4.35 | 5.6 | 3.75 | 1.296 | 496 | 13.4991
|  | Jun | 32.2 | 5.6 | 2.8 | 29.4 | 1.75 | 26 | -0.5 | 0 | 1.25 | 3.75 | 1.296 | 480 | 2.916
|  | Jul | 31.9 | 5.2 | 2.6 | 29.3 | 1.75 | 26 | -0.5 | -0.1 | 1.15 | 3.75 | 1.296 | 496 | 2.7721
|  | Aug | 31.2 | 4.9 | 2.45 | 28.75 | 1.75 | 26 | -0.5 | -0.65 | 0.6 | 3.75 | 1.296 | 496 | 1.4463
|  | Sep | 32.2 | 5.7 | 2.85 | 29.35 | 1.75 | 26 | -0.5 | -0.05 | 1.2 | 3.75 | 1.296 | 480 | 2.7994
|  | Oct | 33.4 | 7.1 | 3.55 | 29.85 | 1.75 | 26 | -0.5 | 0.45 | 1.7 | 3.75 | 1.296 | 496 | 4.098
|  | Nov | 33.9 | 9 | 4.5 | 29.4 | 1.75 | 26 | -0.5 | 0 | 1.25 | 3.75 | 1.296 | 480 | 2.916
|  | Dec | 33.2 | 11.3 | 5.65 | 27.55 | 1.75 | 26 | -0.5 | -1.85 | -0.6 | 3.75 | 1.296 | 496 | -1.4463
|  | TLgw-DEL (KWh) | [12 empty] | 45.2835
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 27°C
|  | Jan | 33.2 | 12.6 | 6.3 | 26.9 | 1.75 | 27 | -1.5 | -2.5 | -2.25 | 3.75 | 1.296 | 496 | -5.4238
|  | Feb | 35.9 | 13.7 | 6.85 | 29.05 | 1.75 | 27 | -1.5 | -0.35 | -0.1 | 3.75 | 1.296 | 448 | -0.21773
|  | Mar | 37.1 | 13 | 6.5 | 30.6 | 1.75 | 27 | -1.5 | 1.2 | 1.45 | 3.75 | 1.296 | 496 | 3.4953
|  | Apr | 38.9 | 11.7 | 5.85 | 33.05 | 1.75 | 27 | -1.5 | 3.65 | 3.9 | 3.75 | 1.296 | 480 | 9.0979
|  | May | 37.8 | 8.1 | 4.05 | 33.75 | 1.75 | 27 | -1.5 | 4.35 | 4.6 | 3.75 | 1.296 | 496 | 11.0886
|  | Jun | 32.2 | 5.6 | 2.8 | 29.4 | 1.75 | 27 | -1.5 | 0 | 0.25 | 3.75 | 1.296 | 480 | 0.5832
|  | Jul | 31.9 | 5.2 | 2.6 | 29.3 | 1.75 | 27 | -1.5 | -0.1 | 0.15 | 3.75 | 1.296 | 496 | 0.36158
|  | Aug | 31.2 | 4.9 | 2.45 | 28.75 | 1.75 | 27 | -1.5 | -0.65 | -0.4 | 3.75 | 1.296 | 496 | -0.96422
|  | Sep | 32.2 | 5.7 | 2.85 | 29.35 | 1.75 | 27 | -1.5 | -0.05 | 0.2 | 3.75 | 1.296 | 480 | 0.46656
|  | Oct | 33.4 | 7.1 | 3.55 | 29.85 | 1.75 | 27 | -1.5 | 0.45 | 0.7 | 3.75 | 1.296 | 496 | 1.6874
|  | Nov | 33.9 | 9 | 4.5 | 29.4 | 1.75 | 27 | -1.5 | 0 | 0.25 | 3.75 | 1.296 | 480 | 0.5832
|  | Dec | 33.2 | 11.3 | 5.65 | 27.55 | 1.75 | 27 | -1.5 | -1.85 | -1.6 | 3.75 | 1.296 | 496 | -3.8569
|  | TLgw-DEL (KWh) | [12 empty] | 16.9011
Thermal Conductive Load (TLgw-x) Calculated for Chennai (Warm and Humid) for Setpoint TSP = 28°C
|  | Jan | 33.2 | 12.6 | 6.3 | 26.9 | 1.75 | 28 | -2.5 | -2.5 | -3.25 | 3.75 | 1.296 | 496 | -7.8343
|  | Feb | 35.9 | 13.7 | 6.85 | 29.05 | 1.75 | 28 | -2.5 | -0.35 | -1.1 | 3.75 | 1.296 | 448 | -2.395
|  | Mar | 37.1 | 13 | 6.5 | 30.6 | 1.75 | 28 | -2.5 | 1.2 | 0.45 | 3.75 | 1.296 | 496 | 1.0848
|  | Apr | 38.9 | 11.7 | 5.85 | 33.05 | 1.75 | 28 | -2.5 | 3.65 | 2.9 | 3.75 | 1.296 | 480 | 6.7651
|  | May | 37.8 | 8.1 | 4.05 | 33.75 | 1.75 | 28 | -2.5 | 4.35 | 3.6 | 3.75 | 1.296 | 496 | 8.678
|  | Jun | 32.2 | 5.6 | 2.8 | 29.4 | 1.75 | 28 | -2.5 | 0 | -0.75 | 3.75 | 1.296 | 480 | -1.7496
|  | Jul | 31.9 | 5.2 | 2.6 | 29.3 | 1.75 | 28 | -2.5 | -0.1 | -0.85 | 3.75 | 1.296 | 496 | -2.049
|  | Aug | 31.2 | 4.9 | 2.45 | 28.75 | 1.75 | 28 | -2.5 | -0.65 | -1.4 | 3.75 | 1.296 | 496 | -3.3748
|  | Sep | 32.2 | 5.7 | 2.85 | 29.35 | 1.75 | 28 | -2.5 | -0.05 | -0.8 | 3.75 | 1.296 | 480 | -1.8662
|  | Oct | 33.4 | 7.1 | 3.55 | 29.85 | 1.75 | 28 | -2.5 | 0.45 | -0.3 | 3.75 | 1.296 | 496 | -0.72317
|  | Nov | 33.9 | 9 | 4.5 | 29.4 | 1.75 | 28 | -2.5 | 0 | -0.75 | 3.75 | 1.296 | 480 | -1.7496
|  | Dec | 33.2 | 11.3 | 5.65 | 27.55 | 1.75 | 28 | -2.5 | -1.85 | -2.6 | 3.75 | 1.296 | 496 | -6.2675
|  | TLgw-DEL (KWh) | [12 empty] | -11.4813
Annual Radiation Thermal Load Through Glass Window
|  | Month | SC | CLF | Max SHGC | Agw-Non op | AC Opn hrs. | TLrad
|  | Jan | 0.55 | 0.51 | 94.63 | 1.296 | 496 | 17.0627
|  | Feb | 0.55 | 0.51 | 104.1 | 1.296 | 448 | 16.9538
|  | Mar | 0.55 | 0.51 | 110.41 | 1.296 | 496 | 19.908
|  | Apr | 0.55 | 0.51 | 123.02 | 1.296 | 480 | 21.4662
|  | May | 0.55 | 0.51 | 164.03 | 1.296 | 496 | 29.5762
|  | Jun | 0.55 | 0.51 | 208.2 | 1.296 | 480 | 36.3295
|  | Jul | 0.55 | 0.51 | 173.5 | 1.296 | 496 | 31.2838
|  | Aug | 0.55 | 0.51 | 129.33 | 1.296 | 496 | 23.3195
|  | Sep | 0.55 | 0.51 | 113.56 | 1.296 | 480 | 19.8155
|  | Oct | 0.55 | 0.51 | 104.1 | 1.296 | 496 | 18.7703
|  | Nov | 0.55 | 0.51 | 94.63 | 1.296 | 480 | 16.5123
|  | Dec | 0.55 | 0.51 | 91.48 | 1.296 | 496 | 16.4947
|  | TLrad | [5 empty] | 267.4925
Inflitration Load for Different Setpoint Temperatures
|  | Month | ACH | Vlivingspace | Cair | ρair | Tdbt | TSP | Tdbt-TSp | Qinf (KJ/h) | KJ/h to W | Qinf (W) | AC opn hrs | Tinf (KWh)
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 22 | 11.2 | 339.5159 | 0.277 | 94.0459 | 496 | 46.6468
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 22 | 13.9 | 421.3635 | 0.277 | 116.7177 | 448 | 52.2895
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 37.1 | 22 | 15.1 | 457.7402 | 0.277 | 126.794 | 496 | 62.8898
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 38.9 | 22 | 16.9 | 512.3052 | 0.277 | 141.9086 | 480 | 68.1161
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 22 | 15.8 | 478.9599 | 0.277 | 132.6719 | 496 | 65.8053
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 22 | 10.2 | 309.202 | 0.277 | 85.6489 | 480 | 41.1115
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 22 | 9.9 | 300.1078 | 0.277 | 83.1299 | 496 | 41.2324
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 22 | 9.2 | 278.8881 | 0.277 | 77.252 | 496 | 38.317
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 22 | 10.2 | 309.202 | 0.277 | 85.6489 | 480 | 41.1115
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.4 | 22 | 11.4 | 345.5787 | 0.277 | 95.7253 | 496 | 47.4797
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 22 | 11.9 | 360.7356 | 0.277 | 99.9238 | 480 | 47.9634
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 22 | 11.2 | 339.5159 | 0.277 | 94.0459 | 496 | 46.6468
|  | Tinf for setpoint 22 degrees C | [11 empty] | 599.6098
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 23 | 10.2 | 309.202 | 0.277 | 85.6489 | 496 | 42.4819
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 23 | 12.9 | 391.0496 | 0.277 | 108.3207 | 448 | 48.5277
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 37.1 | 23 | 14.1 | 427.4263 | 0.277 | 118.3971 | 496 | 58.7249
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 38.9 | 23 | 15.9 | 481.9913 | 0.277 | 133.5116 | 480 | 64.0856
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 23 | 14.8 | 448.646 | 0.277 | 124.2749 | 496 | 61.6404
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 23 | 9.2 | 278.8881 | 0.277 | 77.252 | 480 | 37.081
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 23 | 8.9 | 269.7939 | 0.277 | 74.7329 | 496 | 37.0675
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 23 | 8.2 | 248.5741 | 0.277 | 68.855 | 496 | 34.1521
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 23 | 9.2 | 278.8881 | 0.277 | 77.252 | 480 | 37.081
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.4 | 23 | 10.4 | 315.2648 | 0.277 | 87.3283 | 496 | 43.3149
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 23 | 10.9 | 330.4217 | 0.277 | 91.5268 | 480 | 43.9329
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 23 | 10.2 | 309.202 | 0.277 | 85.6489 | 496 | 42.4819
|  | Tinf for setpoint 23 degrees C | [11 empty] | 550.5716
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 24 | 9.2 | 278.8881 | 0.277 | 77.252 | 496 | 38.317
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 24 | 11.9 | 360.7356 | 0.277 | 99.9238 | 448 | 44.7659
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 37.1 | 24 | 13.1 | 397.1123 | 0.277 | 110.0001 | 496 | 54.5601
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 38.9 | 24 | 14.9 | 451.6774 | 0.277 | 125.1146 | 480 | 60.055
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 24 | 13.8 | 418.3321 | 0.277 | 115.878 | 496 | 57.4755
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 24 | 8.2 | 248.5741 | 0.277 | 68.855 | 480 | 33.0504
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 24 | 7.9 | 239.48 | 0.277 | 66.336 | 496 | 32.9026
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 24 | 7.2 | 218.2602 | 0.277 | 60.4581 | 496 | 29.9872
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 24 | 8.2 | 248.5741 | 0.277 | 68.855 | 480 | 33.0504
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.4 | 24 | 9.4 | 284.9508 | 0.277 | 78.9314 | 496 | 39.15
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 24 | 9.9 | 300.1078 | 0.277 | 83.1299 | 480 | 39.9023
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 24 | 9.2 | 278.8881 | 0.277 | 77.252 | 496 | 38.317
|  | Tinf for setpoint 24 degrees C | [11 empty] | 501.5334
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 25 | 8.2 | 248.5741 | 0.277 | 68.855 | 496 | 34.1521
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 25 | 10.9 | 330.4217 | 0.277 | 91.5268 | 448 | 41.004
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 37.1 | 25 | 12.1 | 366.7984 | 0.277 | 101.6032 | 496 | 50.3952
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 38.9 | 25 | 13.9 | 421.3635 | 0.277 | 116.7177 | 480 | 56.0245
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 25 | 12.8 | 388.0182 | 0.277 | 107.481 | 496 | 53.3106
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 25 | 7.2 | 218.2602 | 0.277 | 60.4581 | 480 | 29.0199
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 25 | 6.9 | 209.166 | 0.277 | 57.939 | 496 | 28.7377
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 25 | 6.2 | 187.9463 | 0.277 | 52.0611 | 496 | 25.8223
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 25 | 7.2 | 218.2602 | 0.277 | 60.4581 | 480 | 29.0199
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.4 | 25 | 8.4 | 254.6369 | 0.277 | 70.5344 | 496 | 34.9851
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 25 | 8.9 | 269.7939 | 0.277 | 74.7329 | 480 | 35.8718
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 25 | 8.2 | 248.5741 | 0.277 | 68.855 | 496 | 34.1521
|  | Tinf for setpoint 25 degrees C | [11 empty] | 452.4951
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 26 | 7.2 | 218.2602 | 0.277 | 60.4581 | 496 | 29.9872
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 26 | 9.9 | 300.1078 | 0.277 | 83.1299 | 448 | 37.2422
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 37.1 | 26 | 11.1 | 336.4845 | 0.277 | 93.2062 | 496 | 46.2303
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 38.9 | 26 | 12.9 | 391.0496 | 0.277 | 108.3207 | 480 | 51.9939
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 26 | 11.8 | 357.7043 | 0.277 | 99.0841 | 496 | 49.1457
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 26 | 6.2 | 187.9463 | 0.277 | 52.0611 | 480 | 24.9893
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 26 | 5.9 | 178.8521 | 0.277 | 49.542 | 496 | 24.5729
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 26 | 5.2 | 157.6324 | 0.277 | 43.6642 | 496 | 21.6574
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 26 | 6.2 | 187.9463 | 0.277 | 52.0611 | 480 | 24.9893
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.4 | 26 | 7.4 | 224.323 | 0.277 | 62.1375 | 496 | 30.8202
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 26 | 7.9 | 239.48 | 0.277 | 66.336 | 480 | 31.8413
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 26 | 7.2 | 218.2602 | 0.277 | 60.4581 | 496 | 29.9872
|  | Tinf for setpoint 26 degrees C | [11 empty] | 403.4569
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 27 | 6.2 | 187.9463 | 0.277 | 52.0611 | 496 | 25.8223
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 27 | 8.9 | 269.7939 | 0.277 | 74.7329 | 448 | 33.4803
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 37.1 | 27 | 10.1 | 306.1706 | 0.277 | 84.8093 | 496 | 42.0654
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 38.9 | 27 | 11.9 | 360.7356 | 0.277 | 99.9238 | 480 | 47.9634
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 27 | 10.8 | 327.3903 | 0.277 | 90.6871 | 496 | 44.9808
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 27 | 5.2 | 157.6324 | 0.277 | 43.6642 | 480 | 20.9588
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 27 | 4.9 | 148.5382 | 0.277 | 41.1451 | 496 | 20.408
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 27 | 4.2 | 127.3185 | 0.277 | 35.2672 | 496 | 17.4925
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 27 | 5.2 | 157.6324 | 0.277 | 43.6642 | 480 | 20.9588
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.4 | 27 | 6.4 | 194.0091 | 0.277 | 53.7405 | 496 | 26.6553
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 27 | 6.9 | 209.166 | 0.277 | 57.939 | 480 | 27.8107
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 27 | 6.2 | 187.9463 | 0.277 | 52.0611 | 496 | 25.8223
|  | Tinf for setpoint 27 degrees C | [11 empty] | 354.4187
|  | Jan | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 28 | 5.2 | 157.6324 | 0.277 | 43.6642 | 496 | 21.6574
|  | Feb | 0.6 | 38.88 | 1.005 | 1.293 | 35.9 | 28 | 7.9 | 239.48 | 0.277 | 66.336 | 448 | 29.7185
|  | Mar | 0.6 | 38.88 | 1.005 | 1.293 | 37.1 | 28 | 9.1 | 275.8567 | 0.277 | 76.4123 | 496 | 37.9005
|  | Apr | 0.6 | 38.88 | 1.005 | 1.293 | 38.9 | 28 | 10.9 | 330.4217 | 0.277 | 91.5268 | 480 | 43.9329
|  | May | 0.6 | 38.88 | 1.005 | 1.293 | 37.8 | 28 | 9.8 | 297.0764 | 0.277 | 82.2902 | 496 | 40.8159
|  | Jun | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 28 | 4.2 | 127.3185 | 0.277 | 35.2672 | 480 | 16.9283
|  | Jul | 0.6 | 38.88 | 1.005 | 1.293 | 31.9 | 28 | 3.9 | 118.2243 | 0.277 | 32.7481 | 496 | 16.2431
|  | Aug | 0.6 | 38.88 | 1.005 | 1.293 | 31.2 | 28 | 3.2 | 97.0045 | 0.277 | 26.8703 | 496 | 13.3276
|  | Sep | 0.6 | 38.88 | 1.005 | 1.293 | 32.2 | 28 | 4.2 | 127.3185 | 0.277 | 35.2672 | 480 | 16.9283
|  | Oct | 0.6 | 38.88 | 1.005 | 1.293 | 33.4 | 28 | 5.4 | 163.6952 | 0.277 | 45.3436 | 496 | 22.4904
|  | Nov | 0.6 | 38.88 | 1.005 | 1.293 | 33.9 | 28 | 5.9 | 178.8521 | 0.277 | 49.542 | 480 | 23.7802
|  | Dec | 0.6 | 38.88 | 1.005 | 1.293 | 33.2 | 28 | 5.2 | 157.6324 | 0.277 | 43.6642 | 496 | 21.6574
|  | Tinf for setpoint 28 degrees C | [11 empty] | 305.3805
Total Internal Load by People
|  | Month | People | SenL/person | CLF | SensL (W) | Latent/Person | LatentL (W) | Total peo L (W) | AC opn hrs |  | Total PL (KWh)
|  | Jan | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Feb | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 448 |  | 188.16
|  | Mar | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Apr | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | May | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Jun | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Jul | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Aug | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Sep | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Oct | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Nov | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 480 |  | 201.6
|  | Dec | 4 | 75 | 1 | 300 | 30 | 120 | 420 | 496 |  | 208.32
|  | Total Internal Load by People | [9 empty] | 2452.8
Total Internal Heat Load of Lights per Year
|  | No. Bulbs | Watt Rating | bf | Fu | CLF | hrs (6hrs/day) | Tihlig(KWh)
|  | 3 | 60 | 1.24 | 0.66 | 0.8 | 2190 | 258.0906
|  | Total Internal Heat Load of Lights per Year | [5 empty] | 258.0906
Total Internal Heat Load-Equipment
|  | TV Rating W | Hrs /day | Total hrs | Tihe (KWh)
|  | 36 | 5 | 1825 | 65.7
|  | Total load Equipment |  |  | 65.7
|  | Tsp | gw-Cond | gw-rad | Tinf | People load | Lighting Load | Equp. Load | All Other Loads
|  | 22 | 158.8131 | 267.4925 | 0 | 2452.8 | 258.0906 | 65.7 | 3202.8963
|  | 23 | 130.4307 | 267.4925 | 0 | 2452.8 | 258.0906 | 65.7 | 3174.5139
|  | 24 | 102.0483 | 267.4925 | 0 | 2452.8 | 258.0906 | 65.7 | 3146.1315
|  | 25 | 73.6659 | 267.4925 | 0 | 2452.8 | 258.0906 | 65.7 | 3117.7491
|  | 26 | 45.2835 | 267.4925 | 0 | 2452.8 | 258.0906 | 65.7 | 3089.3667
|  | 27 | 16.9011 | 267.4925 | 0 | 2452.8 | 258.0906 | 65.7 | 3060.9843
|  | 28 | -11.4813 | 267.4925 | 0 | 2452.8 | 258.0906 | 65.7 | 3032.6019